## Master
Updated 3/28/23
Modify point charts as necessary - add or delete categories needed. Use the energy management system function columns after verifying agency needs. Modify but do not overuse these columns. Include all points that are needed to accomplish the control sequences specified in 23 09 93 and any additional monitoring required. The main purpose of this chart is to clarify what hardware input/output are to be provided by the 23 09 15 contractor. Contact DFD with questions.
Provide a separate set of points per sheet for each unique system and use a separate row for each discrete input/output point. For multiples of identical points indicate the number of points to be provided.
For integrated devices, detail what points should be mapped to the DDC system and make it clear that these are integrated points not hardware points provided by the 23 09 14 contractor. This is especially important to call out what points are required for high point count integration's. The integrated devices should be detailed in a similar manner as the "Software Point" section of the integrated terminal unit controllers which would be bid competatively and are detailed in the point charts at the end of this workbook.
Insert the point charts after specification section 23 09 14 and number consecutively.
MODIFYING THE DFD PROJECT NUMBER AND PROJECT TITLE AND LOCATION ON THIS CHART WILL CHANGE THIS INFORMATION ON ALL THE CHARTS IN THE WORKBOOK. WHEN PRINTING, SELECT ALL THE WORKSHEETS YOU WANT TO PRINT AND THE PAGE NUMBERS WILL AUTOMATICALLY INCREMENT.
DDC INPUT / OUTPUT SUMMARY TABLE
DFD PROJECT NO: 11X1X
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: ENTER / MODIFY EACH SYSTEM NAME INDIVIDUALLY | Control Relay | Solenoid | Contactor | 2-Pos Actuator | Elect/PneuTransducr | Electric Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Run Time | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Point History | Scheduled Start/Stop | Totalization | Trend | Lighting Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION

## 100% OA AHU
DDC INPUT / OUTPUT SUMMARY TABLE | [45 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [40 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: AHU-x (100% OA electrically actuated) | Control Relay | 24VAC | Contactor | 2-Pos Actuator | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Maintenance | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Equipment Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Dry-bulb Economizer | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
Supply Air Temperature | [14 empty] | X | [8 empty] | X | X | [8 empty] | X
Heating Coil Disch Air Temp1 | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [10 empty] | Provide multiple inputs if required. | If a steam coil with face and bypass is provided, call for this point, otherwise delete it.
Reclaim Coil Disch Air Temp | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [11 empty] | Provide this point for units with run-around heat reclaim coils.
Heat Wheel OA Leaving Temp1 | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [10 empty] | Provide multiple inputs if required. | Provide this point for units with heat wheels.
Heat Wheel EA Enterng Temp | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [11 empty] | Provide this point for units with heat wheels.
Heat Wheel EA Lvng Temp | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [11 empty] | Provide this point for units with heat wheels.
Heat Wheel EA Enterng Hum | [15 empty] | X | [7 empty] | X | X | [8 empty] | X | [11 empty] | Provide this point for units with heat wheels.
Heat Wheel OA Lvng Hum | [15 empty] | X | [7 empty] | X | X | [8 empty] | X | [11 empty] | Provide this point for units with heat wheels.
Space Temperature (Room xx) | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [11 empty] | Provide a space temperature point for single zone units. Do not provide if unoccupied cycle is not needed or if DDC terminal units are used.
Space Rel Humidity | [15 empty] | X | [7 empty] | X | X | [8 empty] | X | [10 empty] | Provide (x) sensors - on plans | Utilize this point to reset discharge air humidity setpoint to maintain space humidity. For large spaces, provide mulitple sensors.
Supply Air Rel Humidity | [15 empty] | X | [7 empty] | X | [9 empty] | X | [10 empty] | Provide (2) sensors | Utilize these points to control to discharge air humidity setpoint by using the lowest reading sensor.
Steam Coil Valve | [7 empty] | X | [25 empty] | X | [11 empty] | Modulate both face & bypass dampers and steam valve together above 40 DegF entering air temperature. Call for valve to be 1/4 open before face & bypass modulates. Modulate only face & bypass dampers with steam valve full open below 40 DegF.
Htg Coil Face&Bypass Damper | [7 empty] | X | [25 empty] | X | [11 empty] | Modulate both face & bypass dampers and steam valve together above 40 DegF entering air temperature. Call for valve to be 1/4 open before face & bypass modulates. Modulate only face & bypass dampers with steam valve full open below 40 DegF.
Heating Coil Valve | [7 empty] | X | [25 empty] | X | [11 empty] | Provide this point for hot water heating coils and delete steam coil points. Heating coil discharge temperature point should not be provided with hot water coils.
Reclaim Coil Valve | [7 empty] | X | [25 empty] | X | [11 empty] | Provide this point for units with run-around heat reclaim coils.
Heat Wheel VFD Start/Stop | X | [32 empty] | X | [11 empty] | Provide this point for units with heat wheels.
Heat Wheel VFD Speed | [7 empty] | X | [25 empty] | X | [11 empty] | Provide this point for units with heat wheels.
Heat Wheel Rotation | [11 empty] | X | [21 empty] | X | [11 empty] | Provide this point for units with heat wheels.
Chilled Water Coil Valve | [7 empty] | X | [25 empty] | X
CHW Coil Return Temp | [14 empty] | X | [18 empty] | X
Humidifier Valve | [7 empty] | X | [25 empty] | X | [11 empty] | Modify humidifier specification to provide for electric temperature switch for condensate line and in sequence call for the switch to prove condensate hot before allowing this valve to modulate. Humidifier valve should be provided with humidifier.
Humidifier Manifold Valve |  |  |  | X | [29 empty] | X | [11 empty] | Call for this valve to open on a call for humidity.
OA Damper | [7 empty] | X | [25 empty] | X | [5 empty] | X
OA Damper End Switch | [11 empty] | X | [11 empty] | X | X | [8 empty] | X
Supply Fan VFD Speed | [7 empty] | X | [25 empty] | X | [11 empty] | 0-10VDC outputs to VFD's are preferred to prevent ground loop problems.
Supply Fan Status | [8 empty] | X | [11 empty] | X | [12 empty] | X
Supply Fan Start/Stop | X | [29 empty] | X | X |  | X
Supply Air Static Pressure | [18 empty] | X |  |  |  |  | X | [9 empty] | X
SA Prefilter Differential Press | [16 empty] | X | [6 empty] | X |  | X
SA Final-filter Diff Press | [16 empty] | X | [6 empty] | X |  | X
EA Heat Whl Filter Diff Press | [16 empty] | X | [6 empty] | X |  | X | [19 empty] | Provide this point for units with heat wheels.
Static Shutdown Switch(s) | [11 empty] | X | [8 empty] | X |  | X | [10 empty] | X | [10 empty] | Provide an input for each switch | Call for manual reset static pressure sensorsin sequence. All safties should be hardwired with BAS annuciation through auxiliary contact on safety relay. Include only if ductwork damage can occur. Provide safeties where required to prevent ductwork damage.
Freeze Stat | [11 empty] | X | [8 empty] | X | [12 empty] | X | [10 empty] | Electric freezestat | All safties should be hardwired to fan starter/VFD with BAS annuciation through auxiliary contact on safety relay.
Fire Alarm Shutdown | [11 empty] | X | [8 empty] | X | [12 empty] | X | [9 empty] | X |  | All safties should be hardwired to fan starter/VFD with BAS annuciation through auxiliary contact on safety relay. Coordinate w/Div. 16 designer to provide a fire alarm control module located within 3' of temperature control panel.
Service Shutdown Switch | [10 empty] | X | [22 empty] | X | [11 empty] | This switch is specified to be in each control panel for an AHU. It is to allow maintenance personnel to shutdown the AHU in an orderly manner without alarming the system.
Shutdown Reset Switch | [10 empty] | X | [22 empty] | X | [10 empty] | Reset latchout of supply fans. | This input will reset software latchout of supply fan(s) on failure. Used for redundant supply fan or AHU's or latchout on associated exhaust fan system. Use where required.
Smoke Damper End Switches | [10 empty] | X | [33 empty] | Indicate quantity here. | This input will reset software latchout of supply fan(s) on failure. Used for redundant supply fan or AHU's or latchout on associated exhaust fan system. Use where required.
Smoke Dampers |  |  |  | X | [29 empty] | X | [11 empty] | Smoke dampers can be controlled directly from the BAS by this point. Alternatively, they can be controlled by the Fire Alarm (FA) system, but if in shafts, they will need to close when the airflow has stopped per code. FA monitor module points would need to be added to have the FA system close them when airflow is not present. The smoke damper command point would be deleted with FA control.
Notes:
1. For heat wheel OA leaving and heating coil discharge temperatures, provide multiple inputsfor the number of sensors as required coverage as specified in Section 23 09 14. Sensors shall be individually mapped and averaged in software for control.
Note on A16: If a steam coil with face and bypass is provided, call for this point, otherwise delete it.
Note on A23: Provide a space temperature point in a critical location if the AHU will need to cycle to maintain unoccupied temperature. Do not provide if unoccupied cycle is not needed or if DDC terminal units are used.
Note on A24: Utilize this point to control humdifier.
Note on A25: Utilize this point to limit humdiifier output to 90% supply air relative humidity.
Note on A26: Modulate both face & bypass dampers and steam valve together above 40 DegF entering air temperature. Call for valve to be 1/4 open before face & bypass modulates. Modulate only face & bypass dampers with steam valve full open below 40 DegF.
Note on A27: Modulate both face & bypass dampers and steam valve together above 40 DegF entering air temperature. Call for valve to be 1/4 open before face & bypass modulates. Modulate only face & bypass dampers with steam valve full open below 40 DegF.
Note on A28: Provide this point for hot water heating coils and delete steam coil points. Heating coil discharge temperature point should not be provided with hot water coils.
Note on A29: Provide this point for hot water heating coils and delete steam coil points. Heating coil discharge temperature point should not be provided with hot water coils.
Note on A30: Provide this point for hot water heating coils and delete steam coil points. Heating coil discharge temperature point should not be provided with hot water coils.
Note on A31: Provide this point for hot water heating coils and delete steam coil points. Heating coil discharge temperature point should not be provided with hot water coils.
Note on A32: Provide this point for hot water heating coils and delete steam coil points. Heating coil discharge temperature point should not be provided with hot water coils.
Note on A35: Modify humidifier specification to provide for electric temperature switch for condensate line and in sequence call for the switch to prove condensate hot before allowing this valve to modulate. Humidifier valve should be provided with humidifier.
Note on A36: Call for this two-position valve to open on a call for humidity.
Note on A39: 0-10VDC outputs to VFD's are preferred to prevent ground loop problems.
Note on A46: Call for manual reset static pressure sensorsin sequence. All safties should be hardwired with BAS annuciation through auxiliary contact on safety relay. Include only if ductwork damage can occur. Provide safeties where required to prevent ductwork damage.
Note on A47: All safties should be hardwired to fan starter/VFD with BAS annuciation through auxiliary contact on safety relay.
Note on A48: All safties should be hardwired to fan starter/VFD with BAS annuciation through auxiliary contact on safety relay. Coordinate w/Div. 16 designer to provide a fire alarm control module located within 3' of temperature control panel.
Note on A49: This switch is specified to be in each control panel for an AHU. It is to allow maintenance personnel to shutdown the AHU in an orderly manner without alarming the system.
Note on A50: This input will reset software latchout of supply fan(s) on failure. Used for redundant supply fan or AHU's or latchout on associated exhaust fan system or for smoke damper latchout on supply fan failure to start. Use where required.
Note on A51: Provide for end switch status for smoke dampers required on system. For risers with multiple dampers, two points can be provided for all smoke dampers in a riser to reduce point count. This requires that the smoke dampers have form "C" end switches that are wired in series to prove all smoke dampers open and all smoke dampers closed. Modify point chart if this is used.

## MA AHU
DDC INPUT / OUTPUT SUMMARY TABLE | [45 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [40 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: AHU-x (mixed air VAV electrically actuated) | Control Relay | 24VAC | Contactor | 2-Pos Actuator | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Maintenance | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Equipment Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Dry-bulb Economizer | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
Supply Air Temperature | [14 empty] | X | [8 empty] | X | X | [8 empty] | X
Mixed Air Temperature1 | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [10 empty] | Provide multiple inputs if required.
Return Air Temperature | [14 empty] | X | [8 empty] | X | X | [8 empty] | X
Heating Coil Disch Air Temp1 | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [10 empty] | Provide multiple inputs if required. | If a steam coil with face and bypass is provided, call for this point, otherwise delete it.
Space Temperature (Room xx) | [14 empty] | X | [8 empty] | X | X | [8 empty] | X | [11 empty] | Provide a space temperature point in a critical location if the AHU will need to cycle to maintain unoccupied temperature. Do not provide if unoccupied cycle is not needed or if DDC terminal units are used.
Return Air Rel Humidity | [15 empty] | X | [7 empty] | X | X | [8 empty] | X | [11 empty] | Utilize this point to control humdifier.
Supply Air Rel Humidity | [15 empty] | X | [7 empty] | X | [9 empty] | X | [10 empty] | Supply (2) sensors | Utilize these points to control to discharge air humidity setpoint by using the lowest reading sensor.
Supply Air Flow2 | [19 empty] | X |  |  |  | X | [9 empty] | X | [10 empty] | Provide multiple inputs if required.
Steam Coil Valve | [7 empty] | X | [25 empty] | X | [11 empty] | Modulate both face & bypass dampers and steam valve together above 40 DegF entering air temperature. Call for valve to be 1/4 open before face & bypass modulates. Modulate only face & bypass dampers with steam valve full open below 40 DegF.
Htg Coil Face&Bypass Damper | [7 empty] | X | [25 empty] | X | [11 empty] | Modulate both face & bypass dampers and steam valve together above 40 DegF entering air temperature. Call for valve to be 1/4 open before face & bypass modulates. Modulate only face & bypass dampers with steam valve full open below 40 DegF.
Heating Coil Valve | [7 empty] | X | [25 empty] | X | [11 empty] | Provide this point for hot water heating coils and delete steam coil points. Heating coil discharge temperature point should not be provided with hot water coils.
Chilled Water Coil Valve | [7 empty] | X | [25 empty] | X
CHW Coil Return Temp | [14 empty] | X | [18 empty] | X
Humidifier Valve | [7 empty] | X | [25 empty] | X | [11 empty] | Modify humidifier specification to provide for electric temperature switch for condensate line and in sequence call for the switch to prove condensate hot before allowing this valve to modulate. Humidifier valve should be provided with humidifier.
Humidifier Manifold Valve |  |  |  | X | [29 empty] | X | [11 empty] | Call for this valve to open on a call for humidity.
Return Air Damper | [7 empty] | X | [25 empty] | X | [5 empty] | X | [5 empty] | Override return damper closed if min OA damper is fully open ,and flow setpoint is not met and unit is not in economizer. Limit stroke of return air damper to 50% closed.
Relief Air Damper | [7 empty] | X | [25 empty] | X | [5 empty] | X
Relief Air Static Pressure | [18 empty] | X | [14 empty] | X | [5 empty] | X
Minimum OA Damper | [7 empty] | X | [25 empty] | X | [11 empty] | Modulate minimum outside air damper to maintain minimum outside air flow.
Economizer OA Damper | [7 empty] | X | [25 empty] | X | [5 empty] | X
Minimum OA Flow | [19 empty] | X |  |  |  | X | X | [8 empty] | X
Supply Fan VFD Speed | [7 empty] | X | [25 empty] | X | [11 empty] | 0-10VDC outputs to VFD's are preferred to prevent ground loop problems.
Supply Fan Status | [8 empty] | X | [11 empty] | X | [12 empty] | X
Supply Fan Start/Stop | X | [29 empty] | X | X |  | X
Supply Air Static Pressure | [18 empty] | X |  |  |  |  | X | [9 empty] | X
Return Fan VFD Speed | [7 empty] | X | [25 empty] | X | [11 empty] | 0-10VDC outputs to VFD's are preferred to prevent ground loop problems.
Return Fan Status | [8 empty] | X | [11 empty] | X | [12 empty] | X
Return Fan Start/Stop | X | [29 empty] | X | X |  | X
Return Air Flow2 | [19 empty] | X |  |  |  | X | [9 empty] | X | [10 empty] | Provide multiple inputs if required.
Prefilter Differential Pressure | [16 empty] | X | [6 empty] | X |  | X
Final-filter Differential Pressure | [16 empty] | X | [6 empty] | X |  | X
Static Shutdown Switch(s) | [11 empty] | X | [8 empty] | X |  | X | [21 empty] | Provide an input for each switch | Call for manual reset static pressure sensorsin sequence. All safties should be hardwired with BAS annuciation through auxiliary contact on safety relay. Include only if ductwork damage can occur. Include supply air, mixed air, return air discharge, and return fan inlet safeties where required to prevent ductwork damage.
Freeze Stat | [11 empty] | X | [8 empty] | X | [12 empty] | X | [10 empty] | Electric freezestat | All safties should be hardwired to fan starter/VFD with BAS annuciation through auxiliary contact on safety relay.
Fire Alarm Shutdown | [11 empty] | X | [8 empty] | X | [12 empty] | X | [9 empty] | X |  | All safties should be hardwired to fan starter/VFD with BAS annuciation through auxiliary contact on safety relay. Coordinate w/Div. 16 designer to provide a fire alarm control module located within 3' of temperature control panel.
Service Shutdown Switch | [10 empty] | X | [22 empty] | X | [11 empty] | This switch is specified to be in each control panel for an AHU. It is to allow maintenance personnel to shutdown the AHU in an orderly manner without alarming the system.
Shutdown Reset Switch | [10 empty] | X | [22 empty] | X | [10 empty] | Reset latchout of supply fans. | This input will reset software latchout of supply fan(s) on failure. Used for redundant supply fan or AHU's or latchout on associated exhaust fan system. Use where required.
Smoke Damper End Switches | [10 empty] | X | [33 empty] | Indicate quantity here. | This input will reset software latchout of supply fan(s) on failure. Used for redundant supply fan or AHU's or latchout on associated exhaust fan system. Use where required.
Smoke Dampers |  |  |  | X | [29 empty] | X | [11 empty] | Smoke dampers can be controlled directly from the BAS by this point. Alternatively, they can be controlled by the Fire Alarm (FA) system, but if in shafts, they will need to close when the airflow has stopped per code. FA monitor module points would need to be added to have the FA system close them when airflow is not present. The smoke damper command point would be deleted with FA control.
Notes:
1. For mixed air and heating coil discharge temperatures, provide multiple inputs for the number of sensors as required for coverage as specified in Section 23 09 14. Sensors shall be individually mapped and averaged in software for control.
2. Provide separte flow inputs for each fan in multiple fan systems where flow is measured at the fan.
Note on A18: If a steam coil with face and bypass is provided, call for this point, otherwise delete it.
Note on A19: Provide a space temperature point in a critical location if the AHU will need to cycle to maintain unoccupied temperature. Do not provide if unoccupied cycle is not needed or if DDC terminal units are used.
Note on A20: Utilize this point to control humdifier.
Note on A21: Utilize this point to limit humdiifier output to 90% supply air relative humidity.
Note on A23: Modulate both face & bypass dampers and steam valve together above 40 DegF entering air temperature. Call for valve to be 1/4 open before face & bypass modulates. Modulate only face & bypass dampers with steam valve full open below 40 DegF.
Note on A24: Modulate both face & bypass dampers and steam valve together above 40 DegF entering air temperature. Call for valve to be 1/4 open before face & bypass modulates. Modulate only face & bypass dampers with steam valve full open below 40 DegF.
Note on A25: Provide this point for hot water heating coils and delete steam coil points. Heating coil discharge temperature point should not be provided with hot water coils.
Note on A28: Modify humidifier specification to provide for electric temperature switch for condensate line and in sequence call for the switch to prove condensate hot before allowing this valve to modulate. Humidifier valve should be provided with humidifier.
Note on A29: Call for this two-position valve to open on a call for humidity.
Note on A30: Override return damper closed if min OA damper is fully open ,and flow setpoint is not met and unit is not in economizer. Limit stroke of return air damper to 50% closed.
Note on A31: Override relief damper open if min OA damper is fully open ,and flow setpoint is not met and unit is not in economizer and relief will be needed in minimum outside air mode.
Note on A32: Override relief damper open if min OA damper is fully open ,and flow setpoint is not met and unit is not in economizer and relief will be needed in minimum outside air mode.
Note on A33: Modulate minimum outside air damper to maintain minimum outside air flow.
Note on A36: 0-10VDC outputs to VFD's are preferred to prevent ground loop problems.
Note on A40: 0-10VDC outputs to VFD's are preferred to prevent ground loop problems.
Note on A46: Call for manual reset static pressure sensorsin sequence. All safties should be hardwired with BAS annuciation through auxiliary contact on safety relay. Include only if ductwork damage can occur. Include supply air, mixed air, return air discharge, and return fan inlet safeties where required to prevent ductwork damage.
Note on A47: All safties should be hardwired to fan starter/VFD with BAS annuciation through auxiliary contact on safety relay.
Note on A48: All safties should be hardwired to fan starter/VFD with BAS annuciation through auxiliary contact on safety relay. Coordinate w/Div. 16 designer to provide a fire alarm control module located within 3' of temperature control panel.
Note on A49: This switch is specified to be in each control panel for an AHU. It is to allow maintenance personnel to shutdown the AHU in an orderly manner without alarming the system.
Note on A50: This input will reset software latchout of supply fan(s) on failure. Used for redundant supply fan or AHU's or latchout on associated exhaust fan system or for smoke damper latchout on supply fan failure to start. Use where required.
Note on A51: Provide for end switch status for smoke dampers required on system. For risers with multiple dampers, two points can be provided for all smoke dampers in a riser to reduce point count. This requires that the smoke dampers have form "C" end switches that are wired in series to prove all smoke dampers open and all smoke dampers closed. Modify point chart if this is used.

## HW Heat Exch
DDC INPUT / OUTPUT SUMMARY TABLE | [44 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [39 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: STEAM TO HOT WATER HEAT EXCHANGER HX-x (electrically actuated) | Control Relay | 24VAC | Contactor | 2-Pos Actuator | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Equipment Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Dry-bulb Economizer | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
HOT WATER
Outside Air Temperature | [14 empty] | X | [17 empty] | X | [6 empty] | X |  |  |  | Globally shared point. | Provide outside air temperature on heating system controller to be used on other DDC controllers in the building. If the project entails multiple buildings provide one for each building. For very large buildings, two sensors may be used with a sequence to switch to the backup sensor if the primary sensor fails.
Hot Water Pump 1 S/S | X | [31 empty] | X | [11 empty] | Provide for lead/lag control of pumps.
Hot Water Pump 1 Status | [8 empty] | X | [11 empty] | X | [10 empty] | X | X
HW Pump 1 VFD Speed | [7 empty] | X | [24 empty] | X | [11 empty] | Provide for differential pressure control if pump is 5HP or larger.
Hot Water Pump 2 S/S | X | [31 empty] | X | [11 empty] | Provide for lead/lag control of pumps.
Hot Water Pump 2 Status | [8 empty] | X | [11 empty] | X | [10 empty] | X | X
HW Pump 2 VFD Speed | [7 empty] | X | [24 empty] | X | [11 empty] | Provide for differential pressure control if pump is 5HP or larger.
HW Supply Temp | [14 empty] | X | [8 empty] | X | X | [7 empty] | X | [6 empty] | X |  |  |  |  | Provide for hot water supply temperature reset from outside air temperature.
HW Return Temp | [14 empty] | X | [17 empty] | X
HW Diff Press | [16 empty] | X | [6 empty] | X | X | [7 empty] | X
HW Pump Suction Press | [18 empty] | X |  |  |  |  | X | X | [7 empty] | X | [11 empty] | Show this sensor close to the pump suction to measure the system fill pressure.
HW Heat Exch 1/3 ACV | [7 empty] | X | [24 empty] | X | [11 empty] | If redundant heat exchangers are in the project, arrange for one set of control valves upstream of manual isolation valves on heat exchangers.
HW Heat Exch 2/3 ACV | [7 empty] | X | [24 empty] | X | [11 empty] | If redundant heat exchangers are in the project, arrange for one set of control valves upstream of manual isolation valves on heat exchangers.
Note on A17: Provide outside air temperature on heating system controller to be used on other DDC controllers in the building. If the project entails multiple buildings provide one for each building. For campuses, a campus global sensor may be used and the building sensor would be used if the campus sensor fails or goes offline.
Note on A18: Provide for lead/lag control of pumps.
Note on A20: Provide for differential pressure control if pump is 5HP or larger.
Note on A21: Provide for lead/lag control of pumps.
Note on A23: Provide for differential pressure control if pump is 5HP or larger.
Note on A24: Provide for hot water supply temperature reset from outside air temperature.
Note on A26: Provide multiple differential pressure sensing locations if a very large building or piping/building arrangement will cause uneven loading. Provide the minimum required. Show on plans in a location that will allow servicing and bleeding of pressure lines. Specify a differential pressure setpoint and indicate that the testing and balancing contractor should verify required setpoint during balancing.
Note on A27: Provide multiple differential pressure sensing locations if a very large building or piping/building arrangement will cause uneven loading. Provide the minimum required. Show on plans in a location that will allow servicing and bleeding of pressure lines. Specify a differential pressure setpoint and indicate that the testing and balancing contractor should verify required setpoint during balancing.
Note on A28: If redundant heat exchangers are in the project, arrange for one set of control valves upstream of manual isolation valves on heat exchangers.
Note on A29: If redundant heat exchangers are in the project, arrange for one set of control valves upstream of manual isolation valves on heat exchangers.

## HW Boiler System
DDC INPUT / OUTPUT SUMMARY TABLE | [44 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [39 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: HOT WATER BOILER SYSTEM | Control Relay | 24VAC | Contactor | 2-Pos Actuator | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Equipment Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Dry-bulb Economizer | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments | For boiler systems that are integrated, delete the points that are listed under Integrated Points. For boiler systems that are not integrated, delete the Integrated points list.
POINT DESCRIPTION
HOT WATER
Outside Air Temperature | [14 empty] | X | [17 empty] | X | [6 empty] | X |  |  |  | Globally shared point. | Provide outside air temperature on heating system controller to be used on other DDC controllers in the building. If the project entails multiple buildings provide one for each building. For very large buildings, two sensors may be used with a sequence to switch to the backup sensor if the primary sensor fails.
Boiler System Enable | X | [31 empty] | X
Boiler System Setpoint Reset | [7 empty] | X | [24 empty] | X
Boiler 1 Alarm | [11 empty] | X | [8 empty] | X | [11 empty] | X
Boiler 2 Alarm | [11 empty] | X | [8 empty] | X | [11 empty] | X
Boiler Kill Swtich Status | [11 empty] | X | [8 empty] | X | [11 empty] | X | [11 empty] | Required for boilers over 400,000 Btu/hour. Switch wired to all boiler safety circuits.
Boiler 1 Primary Supply Temp | [14 empty] | X | [8 empty] | X | X | [7 empty] | X | [6 empty] | X |  |  |  |  | Provide for hot water supply temperature reset from outside air temperature.
Boiler 2 Primary Supply Temp | [14 empty] | X | [8 empty] | X | X | [7 empty] | X | [6 empty] | X |  |  |  |  | Provide for hot water supply temperature reset from outside air temperature.
HW Primary Return Temp | [14 empty] | X | [17 empty] | X
HW Secondary Supply Temp | [14 empty] | X | [8 empty] | X | X | [7 empty] | X | [6 empty] | X |  |  |  |  | Provide for hot water supply temperature reset from outside air temperature.
HW Secondary Return Temp | [14 empty] | X | [17 empty] | X
Hot Water Pump 1 S/S | X | [31 empty] | X | [11 empty] | Provide for lead/lag control of pumps.
Hot Water Pump 1 Status | [8 empty] | X | [11 empty] | X | [10 empty] | X | X
HW Pump 1 VFD Speed | [7 empty] | X | [24 empty] | X | [11 empty] | Provide for differential pressure control if pump is 5HP or larger.
Hot Water Pump 2 S/S | X | [31 empty] | X | [11 empty] | Provide for lead/lag control of pumps.
Hot Water Pump 2 Status | [8 empty] | X | [11 empty] | X | [10 empty] | X | X
HW Pump 2 VFD Speed | [7 empty] | X | [24 empty] | X | [11 empty] | Provide for differential pressure control if pump is 5HP or larger.
HW Diff Press | [16 empty] | X | [6 empty] | X | X | [7 empty] | X
HW Pump Suction Press | [18 empty] | X |  |  |  |  | X | X | [7 empty] | X | [11 empty] | Show this sensor close to the pump suction to measure the system fill pressure.
Note on A17: Provide outside air temperature on heating system controller to be used on other DDC controllers in the building. If the project entails multiple buildings provide one for each building. For campuses, a campus global sensor may be used and the building sensor would be used if the campus sensor fails or goes offline.
Note on A23: Provide for hot water supply temperature reset from outside air temperature.
Note on A24: Provide for hot water supply temperature reset from outside air temperature.
Note on A26: Provide for hot water supply temperature reset from outside air temperature.
Note on A28: Provide for lead/lag control of pumps.
Note on A30: Provide for differential pressure control if pump is 5 HP or larger.
Note on A31: Provide for lead/lag control of pumps.
Note on A33: Provide for differential pressure control if pump is 5 HP or larger.

## VFD Integration
DDC INPUT / OUTPUT SUMMARY TABLE | [45 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: VFD POINTS Thru Integrated Communication Interface for all VFD's Provided on Project (excludes heat wheel VFD's) | Control Relay | Solenoid | Contactor | 24 VAC | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Resistive | Differential Pressure | Acutator Feedback | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Occ/Unoc | Totalization | Trend | Redundancy Control | VFD Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | CFM Offset | OA Lockout | CHW Reset | Smoke Control | Fire Alarm Override | Comments | Use this point chart on projects where VFD's are specified to be integrated.
POINT DESCRIPTION
Integrated Points
VFD Total Run Time | [34 empty] | X
KWH | [34 empty] | X
KW | [34 empty] | X
VFD Temperature | [34 empty] | X
Voltage Output | [34 empty] | X
Amperage Output | [34 empty] | X
Output Frequency | [34 empty] | X
Remote Fault Reset | [34 empty] | X
Hand Auto Status | [34 empty] | X
Drive Bypass Status | [34 empty] | X | [9 empty] | On VFD's with Bypass Starters
VFD Fault Status | [34 empty] | X
Notes:
The minimum integrated points listed shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.
Note on A16: Edit the following points for the application.

## Electrical Meter Integration
DDC INPUT / OUTPUT SUMMARY TABLE | [45 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: ELECTRICAL METER POINTS Thru Integrated Communication Interface | Control Relay | Solenoid | Contactor | 24 VAC | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Resistive | Differential Pressure | Acutator Feedback | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Occ/Unoc | Totalization | Trend | Redundancy Control | Meter Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | CFM Offset | OA Lockout | CHW Reset | Smoke Control | Fire Alarm Override | Comments | Use this point chart on projects where VFD's are specified to be integrated.
POINT DESCRIPTION
Integrated Points
Phase A Current | [34 empty] | X
Phase B Current | [34 empty] | X
Phase C Current | [34 empty] | X
Voltage Van | [34 empty] | X
Voltage Vbn | [34 empty] | X
Voltage Vcn | [34 empty] | X
Voltage Vab | [34 empty] | X
Voltage Vbc | [34 empty] | X
Voltage Vca | [34 empty] | X
Phase A Real Power | [34 empty] | X
Phase B Real Power | [34 empty] | X
Phase C Real Power | [34 empty] | X
3 Phase Real Power | [34 empty] | X
3 Phase Reactive Power | [34 empty] | X
3 Phase Apparent Power | [34 empty] | X
Frequency | [34 empty] | X
3 Phase Positve Real Energy Use | [34 empty] | X
3 Phase Reactive Power Demand | [34 empty] | X
Average Phase Current | [34 empty] | X
Average Line Voltage | [34 empty] | X
3 Phase Real Power Demand Max | [34 empty] | X
3 Phase Real Power Demand | [34 empty] | X
3 Phase Apparent Power Demand Max | [34 empty] | X
3 Phase Apparent Power Demand | [34 empty] | X
Notes:
The minimum integrated points listed shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.
Contact user agency for points to be treneded.
Note on A16: Edit the following points for the application.

## Condensate Meter Integration
DDC INPUT / OUTPUT SUMMARY TABLE | [45 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: CONDENSATE METER POINTS Thru Integrated Communication Interface | Control Relay | Solenoid | Contactor | 24 VAC | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Resistive | Differential Pressure | Acutator Feedback | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Occ/Unoc | Totalization | Trend | Redundancy Control | Meter Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | CFM Offset | OA Lockout | CHW Reset | Smoke Control | Fire Alarm Override | Comments | Use this point chart on projects where VFD's are specified to be integrated.
POINT DESCRIPTION
Integrated Points
Volume Rate | [32 empty] | X |  | X
Supply Temperature | [32 empty] | X |  | X
Signal Strength | [34 empty] | X
Speed of Sound | [34 empty] | X
Volume Total Mode 1 | [34 empty] | X
Y-T-D Volume Total Mode 1 | [34 empty] | X
Run Hours | [34 empty] | X
Signal Quality | [34 empty] | X
Meter Status | [34 empty] | X
Flow Direction | [32 empty] | X |  | X
Notes:
The minimum integrated points listed shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.
Note on A16: Edit the following points for the application.

## Steam
DDC INPUT / OUTPUT SUMMARY TABLE | [44 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [39 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: STEAM MONITORING | Control Relay | Solenoid | Contactor | 2-Pos Electric Actuator | Elect/PneuTransducr | Electric Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Equipment Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Manual Changeover | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
STEAM MONITORING
Hi-press Steam Pressure | [17 empty] | X | [5 empty] | X | X | [7 empty] | X | [11 empty] | Delete this point if steam flow computer provides this data through integrated communication interface.
Med-press Steam Pressure | [17 empty] | X | [5 empty] | X | X | [7 empty] | X | [11 empty] | Provide for this point if an intermediate pressure is used for processes within the building or if dual PRV's are used in lieu of a pressure relief line. Provide one for each set of PRV's.
Lo-press Steam Pressure | [17 empty] | X | [5 empty] | X | X | [7 empty] | X | [11 empty] | Delete this point if steam flow computer provides this data through integrated communication interface or if high pressure steam is not present or needs to be monitored.
Steam Flow Rate | [19 empty] | X |  |  |  |  | X | [6 empty] | X | X | [11 empty] | Steam flow should be provided on UW Madison and some other UW and other Agency campuses. Consult with DFD if this point should be provided.
Steam BTU Meter | [11 empty] | X | [19 empty] | X | [12 empty] | Steam BTU metering should be provided on some projects. Consult with DFD if this point and equipment should be provided.
Condensate Rec. High Level | [11 empty] | X | [8 empty] | X | [23 empty] | Provide this point if the agency has standardized on condensate receiver high level alarm monitoring or if the receiver is in a location that will cause damage on overflow. Edit condensate receiver specification to provide for a high level float and cont
Condensate Meter | [11 empty] | X | [8 empty] | X | [10 empty] | X | [12 empty] | Provide this point if the agency has standardized on condensate receiver high level alarm monitoring or if the receiver is in a location that will cause damage on overflow. Edit condensate receiver specification to provide for a high level float and cont
Integrated Steam Flow | [44 empty] | Delete this heading if a steam flow computer is not integrated through an integrated communication interface.
Hi-press Steam Pressure | [23 empty] | X | X | [7 empty] | X | X | [10 empty] | Delete this point if a steam flow computer is not integrated through an integrated communication interface or if high pressure steam is being metered.
Lo-press Steam Pressure | [23 empty] | X | X | [7 empty] | X | X | [10 empty] | Delete this point if a steam flow computer is not integrated through an integrated communication interface or if low pressure steam is being metered.
Steam Flow Rate | [24 empty] | X | [7 empty] | X | X | [10 empty] | Delete this point if a steam flow computer is not integrated through an integrated communication interface.
Steam Heat Rate | [32 empty] | X | X | [10 empty] | Delete this point if a steam flow computer is not integrated through an integrated communication interface.
Steam Mass Total | [24 empty] | X | [7 empty] | X | X | [10 empty] | Delete this point if a steam flow computer is not integrated through an integrated communication interface.
Steam Heat Total | [32 empty] | X | X | [10 empty] | Delete this point if a steam flow computer is not integrated through an integrated communication interface.
Note on A17: Provide for this point if steam is supplied from campus system or a high pressure boiler is provided in the building.
Note on A18: Provide for this point if an intermediate pressure is used for processes within the building or if dual PRV's are used in lieu of a pressure relief line. Provide one for each set of PRV's.
Note on A19: Provide a single pressure transducer for low pressure steam system. Install pressure transducer downstream of PRV station isolation valves if multiple PRV stations are piped in parallel.
Note on A20: Steam flow should be provided on UW Madison and some other UW and other Agency campuses. Consult with DSF if this point should be provided.
Note on A21: Steam BTU metering should be provided on some projects. Consult with DSF if this point and equipment should be provided.
Note on A22: Provide this point if the agency has standardized on condensate receiver high level alarm monitoring or if the receiver is in a location that will cause damage on overflow. Edit condensate receiver specification to provide for a high level float and contacts for BAS.
Note on A23: This point should be provided on campus systems that return condensate to a heating plant. Modify
Note on A26: Provide for this point if steam is supplied from campus system or a high pressure boiler is provided in the building.
Note on A27: Provide a single pressure transducer for low pressure steam system. Install pressure transducer downstream of PRV station isolation valves if multiple PRV stations are piped in parallel.
Note on A28: Steam flow should be provided on UW Madison and some other UW and other Agency campuses. Consult with DSF if this point should be provided.
Note on A29: Steam BTU metering should be provided on some projects. Consult with DSF if this point and equipment should be provided.
Note on A30: Steam flow should be provided on UW Madison and some other UW and other Agency campuses. Consult with DSF if this point should be provided.
Note on A31: Steam BTU metering should be provided on some projects. Consult with DSF if this point and equipment should be provided.

## CHW Campus
DDC INPUT / OUTPUT SUMMARY TABLE | [44 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [39 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Campus Chilled Water System | Control Relay | Solenoid | Contactor | 2-Pos Electric Actuator | Elect/PneuTransducr | Electric Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Equipment Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Manual Changeover | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
CHILLED WATER
Chilled Water Pump S/S | X | [31 empty] | X
Chilled Water Pump Status | [8 empty] | X | [11 empty] | X | [10 empty] | X | X
Chilled Water Diff Press | [16 empty] | X | [6 empty] | X | [8 empty] | X
CHW Pump VFD Speed | [6 empty] | X | [25 empty] | X
CHW Pump Status | [8 empty] | X | [11 empty] | X | [11 empty] | X
Chilled Water Bypass Valve |  | X | [30 empty] | X
Winter CHW Pump S/S | X | [31 empty] | X
Winter CHW Pump Status | [8 empty] | X | [11 empty] | X | [10 empty] | X | X
Integrated Points | [44 empty] | Delete Integrated Points heading if a CHW BTU computer is not integrated through a communication interace.
Campus CHWS Temperature | [23 empty] | X | [8 empty] | X | X | [10 empty] | Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Campus CHWR Temperature | [23 empty] | X | [8 empty] | X | X | [10 empty] | Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Chilled Water Volume Rate | [31 empty] | X | X | X | [10 empty] | Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Chilled Water Energy Rate | [31 empty] | X | X | X | [10 empty] | Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Energy Total | [32 empty] | X | X | [10 empty] | Delete point if not integrated through communication interface on BTU measurement system.
Zero Energy Total | [33 empty] | X | [10 empty] | Delete point if not integrated through communication interface on BTU measurement system.
Volume Total | [32 empty] | X | X | [10 empty] | Delete point if not integrated through communication interface on BTU measurement system.
Zero Volume Total | [33 empty] | X | [10 empty] | Delete point if not integrated through communication interface on BTU measurement system.
Note on A17: If redundant pumps are provided, provide for lead/lag control.
Note on A19: Provide multiple differential pressure sensing locations if a very large building or piping/building arrangement will cause uneven loading. Provide the minimum required. Show on plans in a location that will allow servicing and bleeding of pressure lines. Specify a differential pressure setpoint and indicate that the testing and balancing contractor should verify required setpoint during balancing.
Note on A22: Provide for this valve around the chilled water pumps in campus systems where the system pressure can be used to pump the building. Open if differential pressure sensor is above setpoint and CHW pump VFD is at minimum for 15 minutes. Close and start pump if differential pressure falls below setpoint for 15 minutes.
Note on A23: Provide for this pump in buildings that utilize chilled water in the winter for reduced loads such as process chilled water, refrigerant condensors, or spot cooling with fan coil units.
Note on A27: Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Note on A28: Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Note on A29: Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Note on A30: Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Note on A31: Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Note on A32: Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Note on A33: Add hardware checkmark if not integrated through communication interface on BTU measurement system.
Note on A34: Add hardware checkmark if not integrated through communication interface on BTU measurement system.

## CHW Chiller
DDC INPUT / OUTPUT SUMMARY TABLE | [44 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [39 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Chiller (One Chiller System) | Control Relay | Solenoid | Contactor | 2-Pos Actuator | Elect/PneuTransducr | Electric Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Equipment Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Manual Changeover | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
CHILLED WATER
Chiller Enable | X | [31 empty] | X
CHW Primary Pump Status | [8 empty] | X | [23 empty] | X
CHW Sec Supply Temperature | [14 empty] | X | [8 empty] | X | [8 empty] | X
CHW Sec Return Temperature | [14 empty] | X | [17 empty] | X
CHW Sec Differential Press | [16 empty] | X | [6 empty] | X | X | [7 empty] | X
Secondary CHW Pump S/S | X | [31 empty] | X
Secondary CHW Pump Status | [8 empty] | X | [11 empty] | X | [10 empty] | X | X
Sec CHW Pump VFD Speed | [6 empty] | X | [25 empty] | X
CW Entering Chiller Temp | [14 empty] | X | [17 empty] | X |  |  |  |  | X
Cond Water Leaving Temp | [32 empty] | X |  |  |  |  | X
Cond Water Pump Status | [8 empty] | X | [23 empty] | X
Cond Water Bypass Valve |  |  |  |  | X | [27 empty] | X
Clg Tower Fan S/S | X | [31 empty] | X
Clg Tower Fan Status | [8 empty] | X | [11 empty] | X | [10 empty] | X | X
Clg Tower Fan VFD Speed | [6 empty] | X | [25 empty] | X
Outside Air Temperature | [14 empty] | X | [17 empty] | X
Outside Air Humidity | [15 empty] | X | [16 empty] | X
Integrated Points | [44 empty] | For chiller systems that are not integrated, revise the Integrated points to hardwired points.
Chiller Alarm | [20 empty] | X | [16 empty] | X
Chiller Setpoint Reset | [32 empty] | X |  |  |  |  | X
Chiller Demand Reset | [32 empty] | X |  |  |  |  | X
CHW Primary Supply Temp | [32 empty] | X |  |  |  |  | X
CHW Primary Return Temp | [32 empty] | X |  |  |  |  | X
Notes:
The minimum integrated points listed shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.
Note on AA13: If VFD is integrated into the DDC system, delete this point.
Note on A17: Starting of lag chiller should be based on secondary chilled water supply temperature being above setpoint by 2 DegF for 15 minutes. Shutting down of lag chiller should be based on the secondary supply and return temperature differential falling below a given setpoint for 15 minutes. All setpoints and timers should be called out to be adjustable. If another strategy is to be used, consult with DSF.
Note on A18: Primary pump should be controlled directly from the chiller. Call for start/stop of this pump to wired to chiller controls by temperature control contractor.
Note on A21: Provide multiple differential pressure sensing locations if a very large building or piping/building arrangement will cause uneven loading. Provide the minimum required. Show on plans in a location that will allow servicing and bleeding of pressure lines. Specify a differential pressure setpoint and indicate that the testing and balancing contractor should verify required setpoint during balancing.
Note on A25: This temperature should be used for condensor water temperature control and should be a hardwired temperature sensor. If not used for control, this can be an integrated only point.
Note on A26: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A27: Condensor water pump should be controlled directly from the chiller. Call for start/stop of this pump to wired to chiller controls by temperature control contractor.
Note on A28: Provide for a condensor water bypass valve only if the chilled water system needs to run at low ambient conditions.
Note on A32: Provide for this point if there is not a global outside air temperature point available on the automation system in the building which houses the chiller.
Note on A33: Provide for this point if cooling tower approach condensor water temperature control strategy is used.
Note on A36: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A37: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A38: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A39: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A40: Provide hardware check mark if point is not provided through integrated communication interface.

## Mult CHW Chiller
DDC INPUT / OUTPUT SUMMARY TABLE | [44 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [39 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Chiller (Two Chiller System) | Control Relay | Solenoid | Contactor | 2-Pos Actuator | Elect/PneuTransducr | Electric Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Lead/Lag Control | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Equipment Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Manual Changeover | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
CHILLED WATER
Chiller CH-1 Enable | X | [31 empty] | X
CH-1 Primary Pump Status | [8 empty] | X | [11 empty] | X | [11 empty] | X
Chiller CH-2 Enable | X | [31 empty] | X
CH-2 Primary Pump Status | [8 empty] | X | [11 empty] | X | [11 empty] | X
CHW Sec Supply Temperature | [14 empty] | X | [8 empty] | X | [8 empty] | X
CHW Sec Return Temperature | [14 empty] | X | [17 empty] | X
CHW Sec Differential Press | [16 empty] | X | [6 empty] | X | X | [7 empty] | X
Secondary CHW Pump S/S | X | [31 empty] | X
Secondary CHW Pump Status | [8 empty] | X | [11 empty] | X | [11 empty] | X
Sec CHW Pump VFD Speed | [6 empty] | X | [18 empty] | X | [5 empty] | X | X
CW Entering Chiller Temp | [14 empty] | X | [17 empty] | X
CW Leaving CH-1 Temp | [14 empty] | X | [17 empty] | X
CW Leaving CH-2 Temp | [14 empty] | X | [17 empty] | X
CH-1 Cond Water Pump Status | [8 empty] | X | [11 empty] | X | [11 empty] | X
CH-2 Cond Water Pump Status | [8 empty] | X | [11 empty] | X | [11 empty] | X
Cond Water Bypass Valve |  |  |  |  | X | [27 empty] | X
Clg Tower Fan 1 S/S | X | [31 empty] | X
Clg Tower Fan 1 Status | [8 empty] | X | [11 empty] | X | [11 empty] | X
Clg Tower Fan 1 VFD Speed | [6 empty] | X | [18 empty] | X | [5 empty] | X | X
Clg Tower Fan 2 S/S | X | [31 empty] | X
Clg Tower Fan 2 Status | [8 empty] | X | [11 empty] | X | [11 empty] | X
Clg Tower Fan 2 VFD Speed | [6 empty] | X | [18 empty] | X | [5 empty] | X | X
Outside Air Temperature | [14 empty] | X | [17 empty] | X
Outside Air Humidity | [15 empty] | X | [16 empty] | X
Integrated Points | [44 empty] | For chiller systems that are not integrated, revise the Integrated points to hardwired points.
Chiller CH-1 Alarm | [20 empty] | X | [16 empty] | X
Chiller CH-1 Setpoint Reset | [32 empty] | X |  |  |  |  | X
Chiller CH-1 Demand Reset | [32 empty] | X |  |  |  |  | X
CH-1 CHW Primary Sup Temp | [32 empty] | X |  |  |  |  | X
CH-1 CHW Primary Ret Temp | [32 empty] | X |  |  |  |  | X
Chiller CH-2 Alarm | [20 empty] | X | [16 empty] | X
Chiller CH-2 Setpoint Reset | [32 empty] | X |  |  |  |  | X
Chiller CH-2 Demand Reset | [32 empty] | X |  |  |  |  | X
CH-2 CHW Primary Sup Temp | [32 empty] | X |  |  |  |  | X
CH-2 CHW Primary Ret Temp | [32 empty] | X |  |  |  |  | X
Notes:
The minimum integrated points listed shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.
Note on A18: Primary pump should be controlled directly from the chiller. Call for start/stop of this pump to wired to chiller controls by temperature control contractor.
Note on A20: Primary pump should be controlled directly from the chiller. Call for start/stop of this pump to wired to chiller controls by temperature control contractor.
Note on A23: Provide multiple differential pressure sensing locations if a very large building or piping/building arrangement will cause uneven loading. Provide the minimum required. Show on plans in a location that will allow servicing and bleeding of pressure lines. Specify a differential pressure setpoint and indicate that the testing and balancing contractor should verify required setpoint during balancing.
Note on A27: This temperature should be used for condensor water temperature control.
Note on A30: Condensor water pump should be controlled directly from the chiller. Call for start/stop of this pump to wired to chiller controls by temperature control contractor. If a single pump is used for more than one chiller, a call for condensor water pump run digital input should be called out from each chiller and used to start the common pump. There will also be a need to add isolation valves for the condensor water to each chiller.
Note on A31: Condensor water pump should be controlled directly from the chiller. Call for start/stop of this pump to wired to chiller controls by temperature control contractor. If a single pump is used for more than one chiller, a call for condensor water pump run digital input should be called out from each chiller and used to start the common pump. There will also be a need to add isolation valves for the condensor water to each chiller.
Note on A32: Provide for a condensor water bypass valve only if the chilled water system needs to run at low ambient conditions.
Note on A33: Stage the tower fans on based on temperature but run fans in parallel at reduced speeds for energy savings. When lead fan is running at 50% or more for 15 minutes stage on lag fan and run at same speed in parallel. When both fans are running at minimum speed for 15 minutes, stage off lag fan.
Note on A35: The cooling tower fans should be run in parallel at a common speed. Bring on lag tower fan when lead fan speed is above 50%. Turn off lag fan when condensor water is below setpoint by 2 DegF adn both fans are at minimum speed for 15 minutes. Call for all setpoints and timers to be adjustable.
Note on A36: Stage the tower fans on based on temperature but run fans in parallel at reduced speeds for energy savings. When lead fan is running at 50% or more for 15 minutes stage on lag fan and run at same speed in parallel. When both fans are running at minimum speed for 15 minutes, stage off lag fan.
Note on A38: The cooling tower fans should be run in parallel at a common speed. Bring on lag tower fan when lead fan speed is above 50%. Turn off lag fan when condensor water is below setpoint by 2 DegF adn both fans are at minimum speed for 15 minutes. Call for all setpoints and timers to be adjustable.
Note on A39: Provide for this point if there is not a global outside air temperature point available on the automation system in the building which houses the chiller.
Note on A40: Provide for this point if cooling tower approach condensor water temperature control strategy is used.
Note on A43: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A44: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A45: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A46: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A47: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A48: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A49: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A50: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A51: Provide hardware check mark if point is not provided through integrated communication interface.
Note on A52: Provide hardware check mark if point is not provided through integrated communication interface.

## Misc
DDC INPUT / OUTPUT SUMMARY TABLE | [44 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [39 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Miscellaneous Points | Control Relay | Solenoid | Contactor | 2-Pos Actuator | Elect/PneuTransducr | Electric Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Relative Humidity | Differential Pressure | Gauge Pressure | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Lighting Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | Manual Changeover | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
COLD ROOMS
Room Temperature | [14 empty] | X | [8 empty] | X | X | [7 empty] | X | [11 empty] | If cold room is coming with an integral controller or chart recorder, coordinate with cold room designer to provide a 0-10VDC or 4-20mA temperature signal output to the BAS and call this out in the temperature control specification.
Room Humidity | [15 empty] | X | [7 empty] | X | [8 empty] | X | [11 empty] | Provide only if program requires this. If cold room is coming with an integral controller or chart recorder, coordinate with cold room designer to provide a 0-10VDC or 4-20mA humidity signal output to the BAS and call this out in the temperature control specification.
Knox Box | [44 empty] | Provide this point on UW Madison campus projects only.
Knox Box Alarm | [11 empty] | X | [8 empty] | X | [22 empty] | Open Contacts = Alarm
Steam Pit Alarms | [44 empty] | Provide this point on UW Madison campus projects only unless requested by Agency.
Sump High Level Alarm | [11 empty] | X | [8 empty] | X | [22 empty] | Open Contacts = Alarm
Sump Power Failure | [11 empty] | X | [8 empty] | X | [22 empty] | Open Contacts = Alarm
Fire Alarm/Protection | [44 empty] | Contact the Agency to verify if secondary fire alarm reporting is done through the building automation system to see if these points should be provided. For UW Madison projects, add a comment to provide a stand-alone controller for the fire alarm points. The following Universities use fire alarm reporting through their BAS: UW Madison, Parkside, Stout, and Milwaukee. Area of rescue assistance is only provided at UW Madison. The other UW's do not need fire alarm panel reporting as they use other means of central reporting.
Alarm | [11 empty] | X | [8 empty] | X | [22 empty] | Open Contacts = Alarm
Trouble | [11 empty] | X | [8 empty] | X | [22 empty] | Open Contacts = Alarm
Supervisory | [11 empty] | X | [8 empty] | X | [22 empty] | Open Contacts = Alarm | Contact the Agency to determine if a separate supervisory point is required. This is required for UW Madison projects.
Area of Rescue Assistance | [11 empty] | X | [8 empty] | X | [22 empty] | Open Contacts = Alarm | This point is only provided for UW Madison projects. This point should reside on the fire alarm reporting controller. Coordinate with Division 26 designer to provide for dry contacts in area of rescue assistance annuciator panel for connection to BAS.
Note on A18: If cold room is coming with an integral controller or chart recorder, coordinate with cold room designer to provide a 0-10VDC or 4-20mA temperature signal output to the BAS and call this out in the temperature control specification.
Note on A19: Provide only if program requires this. If cold room is coming with an integral controller or chart recorder, coordinate with cold room designer to provide a 0-10VDC or 4-20mA humidity signal output to the BAS and call this out in the temperature control specification.
Note on A21: Provide this point on UW Madison campus projects only.
Note on A22: Provide this point on UW Madison campus projects only.
Note on A24: Provide this point on UW Madison campus projects only.
Note on A25: Provide this point on UW Madison campus projects only.
Note on A26: Provide this point on UW Madison campus projects only.
Note on A28: Contact the Agency to verify if secondary fire alarm reporting is done through the building automation system to see if these points should be provided. For UW Madison projects, add a comment to provide a stand-alone controller for the fire alarm points. The following Universities use fire alarm reporting through their BAS: UW Madison, Parkside, Stout, and Milwaukee. Area of rescue assistance is only provided at UW Madison. The other UW's do not need fire alarm panel reporting as they use other means of central reporting.
Note on A31: Contact the Agency to determine if a separate supervisory point is required. This is required for UW Madison projects.
Note on A32: For UW Madison projects, provide a separate point for each rescue location. These points do not need to reside on the fire alarm reporting controller. Coordinate with Division 16 designer to provide for dry contacts in area of rescue assistance annuciator panel for connection to BAS.

## SupExh VAV
DDC INPUT / OUTPUT SUMMARY TABLE | [45 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [40 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Supply/Exhaust Matching VAV Terminals (See plans for Qty) | Control Relay | Solenoid | Contactor | 24 VAC | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Resistive | Differential Pressure | Acutator Feedback | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Occ/Unoc | Totalization | Trend | Redundancy Control | Lighting Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | CFM Offset | OA Lockout | CHW Reset | Smoke Control | Fire Alarm Override | Comments | Only check hardware I/O columns for points that will be wired by the 23 09 14 contractor. If there are points that should be shown that are integral to the controller, put the points in the "Point Description" column, edit and check an appropriate software column, and provide an explanation in the comment column. Utilize proportional (0-10VDC or 4-20mA) acutation where possible. On some negotiated projects, the controller will have a limited number of proportional outputs available and it may be necessary to utilize a tri-state or duration adjust type output for actuation.
POINT DESCRIPTION
Zone Temperature | [14 empty] | X | [8 empty] | X | X | [7 empty] | X
Temperature Setpoint Adjust5 | [15 empty] | X | [28 empty] | Integral w/Sensor
Occupancy Sensor | [11 empty] | X
Supply Air Damper 1 & 2 |  |  |  |  | X | X | X | X | [9 empty] | X
Supply Air Flow | [32 empty] | X
Discharge Air Temperature | [14 empty] | X | [17 empty] | X
Reheat Valve 1 |  |  |  |  | X | X | X | X | [9 empty] | X
HW Radiation ACV 3 |  |  |  |  | X | X | X | X | [32 empty] | X |  |  |  |  | Determine if this actuator should be proportional, tri-state, or a duration adjust type output.
General Exhaust Damper 1 & 2 |  |  |  |  | X | X | X | X | [9 empty] | X
General Exhaust Air Flow | [16 empty] | X | [15 empty] | X
Software Points 4
Occupied Heating Setpoint
Occupied Cooling Setpoint
Unoccupied Heating Setpoint
Unoccupied Cooling Setpoint
Standby Heating Setpoint
Standby Cooling Setpoint
Exhaust Flow Differential Setpoint
Radiation Lockout Command
Occ/Unoc/Standby Command | [30 empty] | X
Actual Supply Flow Setpoint | [32 empty] | X
Actual Exhaust Flow Setpoint | [32 empty] | X
Actual Heating Setpoint | [32 empty] | X
Actual Cooling Setpoint | [32 empty] | X
Temperature Setpoint Adjust Range 5
Notes:
1. Analog outputs must utilize a calculated proportional command from software. Actual output can be any type but floating outputs shall have feedback from the acutator so actual actuator position is known.
2. Damper actuators can utilize stepper type motors.
3. Can be tri-state or proportional actuation.
4. The minimum software points listed, if necessary to the application, shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.
5. Separate heating and cooling setpoints are preferred. If temperature setpoint is a single input that will offset the heating and cooling supervisory setpoints up or down together by an adjustable range.
Note on A17: Include if supply air system runs continously during unoccupied mode and this input is desired.
Note on A18: On negotiated projects, indicate whether this is integral to the VAV controller.
Note on A19: On negotiated projects, indicate whether this is integral to the VAV controller.
Note on A26: Edit the following points for the application.

## Sup VAV
DDC INPUT / OUTPUT SUMMARY TABLE | [45 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [40 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Supply VAV Terminals (See plans for Qty) | Control Relay | Solenoid | Contactor | 24 VAC | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Resistive | Differential Pressure | Actuator Feedback | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Occ/Unoc | Totalization | Trend | Redundancy Control | Lighting Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | CFM Offset | OA Lockout | CHW Reset | Smoke Control | Fire Alarm Override | Comments | Only check hardware I/O columns for points that will be wired by the 23 09 14 contractor. If there are points that should be shown that are integral to the controller, put the points in the "Point Description" column and provide an explanation in the comment column. Utilize proportional (0-10VDC or 4-20mA) acutation where possible. On some negotiated projects, the controller will have a limited number of proportional outputs available and it may be necessary to utilize a tri-state or duration adjust type output for actuation.
POINT DESCRIPTION
Zone Temperature | [14 empty] | X | [8 empty] | X | X | [7 empty] | X
Temperature Setpoint Adjust5 | [15 empty] | X | [28 empty] | Integral w/Sensor
Unnocupied Override Button | [10 empty] | X | [33 empty] | Integral w/Sensor
Occupancy Sensor | [11 empty] | X
Supply Air Damper 1 & 2 |  |  |  |  | X | X | X | X | [9 empty] | X
Supply Air Flow | [19 empty] | X | [12 empty] | X
Discharge Air Temperature | [14 empty] | X | [17 empty] | X
Reheat Valve 1 |  |  |  |  | X | X | X | X | [9 empty] | X | [14 empty] | X
HW Radiation ACV 3 | [7 empty] | X | [24 empty] | X | [7 empty] | X
Software Points 4
Occupied Heating Setpoint
Occupied Cooling Setpoint
Unoccupied Heating Setpoint
Unoccupied Cooling Setpoint
Standby Heating Setpoint
Standby Cooling Setpoint
Radiation Lockout Command
Occupied/Unoccupied Command 7 & 10 | [30 empty] | X
Actual Flow Setpoint | [32 empty] | X
Actual Heating Setpoint | [32 empty] | X
Actual Cooling Setpoint | [32 empty] | X
Temperature Setpoint Adjust Range 5
Notes:
1. Analog outputs must utilize a calculated proportional command from software. Actual output can be any type but floating outputs shall have feedback from the acutator so actual actuator position is known.
2. Damper actuators can utilize stepper type motors.
3. Can be tri-state or proportional actuation.
4. The minimum software points listed, if necessary to the application, shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.
5. Separate heating and cooling setpoints are preferred. If temperature setpoint is a single input that will offset the heating and cooling supervisory setpoints up or down together by an adjustable range.
Note on A18: Include if supply air system runs continously during unoccupied mode and this input is desired.
Note on A19: Actuator should be 0-10VDC, 4-20mA, Duration Adjust, or Tri-State with feedback. On negotiated DDC control projects, indicate if this integral to the controller.
Note on A20: On negotiated projects, indicate whether this is integral to the VAV controller.
Note on A22: Actuator should be 0-10VDC, 4-20mA, Duration Adjust, or Tri-State with feedback.
Note on A23: Actuator should be 0-10VDC, Duration Adjust, or Tri-State.

## Fan Coil
DDC INPUT / OUTPUT SUMMARY TABLE | [45 empty] | Designer instructions - incorporate point comments into sequence of operations.
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [40 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Fan Coil Unit Control (See plans for Qty) | Control Relay | Solenoid | Contactor | 24 VAC | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Resistive | Differential Pressure | Actuator Feedback | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Redundancy Control | Lighting Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | CFM Offset | HW/OA Reset | CHW Reset | Smoke Control | Fire Alarm Override | Comments | Only check hardware I/O columns for points that will be wired by the 23 09 14 contractor. If there are points that should be shown that are integral to the controller or software type points, put the points in the "Point Description" column, edit and check
POINT DESCRIPTION
Zone Temperature | [14 empty] | X | [8 empty] | X | X | [7 empty] | X
Discharge Air Temperature | [14 empty] | X | [17 empty] | X
Temperature Setpoint Adjust 2 | [14 empty] | X | [17 empty] | X
Heating Valve | [7 empty] | X | [9 empty] | X | [14 empty] | X
Cooling Valve | [7 empty] | X | [9 empty] | X | [14 empty] | X
Fan Start/Stop | X | [31 empty] | X | [12 empty] | Revise for speed control if agency wants multiple speed adjustments. This is typically high-medium-low.
Fan Status | [8 empty] | X | [23 empty] | X
Mixed Air Dampers 1 |  |  |  |  | X |  |  | X | [9 empty] | X | [14 empty] | X
Mixed Air Temperature | [14 empty] | X | [17 empty] | X
Notes:
1. Analog outputs must utilize a calculated proportional command from software. Actual output can be any type but floating outputs shall have feedback from the acutator so actual actuator position is known.
2. Separate heating and cooling setpoints are preferred. If temperature setpoint is a single input that will offset the heating and cooling supervisory setpoints up or down together by an adjustable range.

## Reheat
DDC INPUT / OUTPUT SUMMARY TABLE
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [41 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Constant Volume Reheat Terminals (See plans for Qty) | Control Relay | Solenoid | Contactor | 24 VAC | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Resistive | Differential Pressure | Feedback for Tri-State | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Run Time | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Redundancy Control | Lighting Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | CFM Offset | OA Lockout | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
Hardware Points
Zone Temperature | [14 empty] | X | [8 empty] | X | X | [8 empty] | X
Temperature Setpoint Adjust 4 | [15 empty] | X
Discharge Air Temperature | [14 empty] | X | [18 empty] | X
Reheat Valve 1 |  |  |  |  | X |  |  | X | [9 empty] | X | [15 empty] | X
HW Radiation ACV 2 |  |  |  |  | X |  |  | X | [25 empty] | X | [7 empty] | X |  |  |  | Where applicable - see plans.
Software Points (Mapped)3
Occupied Heating Setpoint
Occupied Cooling Setpoint
Unoccupied Heating Setpoint
Unoccupied Cooling Setpoint
Radiation Lockout Command
Occupied/Unoccupied Command
Actual Heating Setpoint | [33 empty] | X
Actual Cooling Setpoint | [33 empty] | X
Temperature Setpoint Adjust Range 4
Notes:
1. Analog outputs must utilize a calculated proportional command from software. Actual output can be any type but floating outputs shall have feedback from the acutator so actual actuator position is known.
2. Can be tri-state or proportional actuation.
3. The minimum software points listed, if necessary to the application, shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.
4. Separate heating and cooling setpoints are preferred. If temperature setpoint is a single input that will offset the heating and cooling supervisory setpoints up or down together by an adjustable range.

## Stand-alone Radiation
DDC INPUT / OUTPUT SUMMARY TABLE
DFD PROJECT NO: 11X1X |  |  |  |  | DDC CONTROLLERS PROVIDED UNDER SPECIFICATION SECTION 23 09 2x | [41 empty] | EDIT EACH CHART FOR APPROPRIATE SECTION TO PROVIDE CONTROLLERS
PROJECT: | HARDWARE | [19 empty] | SOFTWARE
PROJECT TITLE
LOCATION: | OUTPUT | [7 empty] | INPUT | [11 empty] | ALARMS
PROJECT LOCATION
| DIGITAL |  |  |  | ANALOG |  |  |  | DIGITAL | [5 empty] | ANALOG | [5 empty] | DIGITAL |  |  | ANALOG |  |  | ENERGY MANAGEMENT SYSTEM FUNCTIONS
SYSTEM: Stand-Alone Radiation (See plans for Qty) | Control Relay | Solenoid | Contactor | 24 VAC | Tri-State Actuator | Duration Adjust Actuator | 4-20 mA | 0-10 VDC | Current Sensing Switch | Control Relay Contact | Switch Closure | Auxiliary Contact | Diff Pressure Switch | Flow Switch | Temperature | Resistive | Differential Pressure | Feedback for Tri-State | Static Pressure | Flow | Equipment Status | Maintenance | Pressure | High Limit | Low Limit | Run Time | Day/Night Setback | Demand Limiting | Dial-up I/O | Duty Cycling | Optimum Start/Stop | Scheduled Start/Stop | Totalization | Trend | Redundancy Control | Lighting Integration | Fire Alarm Integration | Security/Access Integration | Elect PQM Integration | Chiller Integration | CFM Offset | OA Lockout | CHW Reset | Smoke Control | Fire Alarm Override | Comments
POINT DESCRIPTION
Hardware Points
Zone Temperature | [14 empty] | X | [8 empty] | X | X | [8 empty] | X
Temperature Setpoint Adjust | [15 empty] | X
HW Return Temperature | [14 empty] | X | [18 empty] | X | [11 empty] | Strap-on element
HW Radiation ACV | [7 empty] | X | [25 empty] | X | [7 empty] | X
Software Points (Mapped) 1
Occupied Heating Setpoint
Unoccupied Heating Setpoint
Radiation Lockout Command
Occupied/Unoccupied Command
Actual Heating Setpoint | [33 empty] | X
Temperature Setpoint Adjust Range 4
Notes:
1. The minimum software points listed, if necessary to the application, shall be mapped. Any additional software points that are available and requested by the user Agency shall be mapped by the DDC contractor.