## Sheet1
DFD Naming Conventions for Mechanical Equipment
Updated 12/6/2023
General Notes:
Numbering below is for example only. Numbering should be sequential and should not result in duplicate tags for any piece of equipment.
If there is only a single element within a mechanical system do not use system letters, i.e. AHU's that are not manifolded would be AHU-1, AHU-2, AHU-3, etc., two separate chilled water systems with a single pump would be CHWP-1, CHWP-2.
For systems that are manifolded, use sequential numbers by system. Elements within the manifolded system use system letters to designate each element, i.e. the first AHU system with (3) AHU's that are manifolded would be AHU-1A, AHU-1B & AHU-1C, a second hot water system with two HX's that are piped in parallel would be HX-2A & HX-2B, two manifolded pumps for the third process chilled water system would be PCP-3A & PCP-3B.
For terminals or systems that are not listed, use a Tag that is an appropriate acronym and when applicable, use the same system/floor/sequential format as designated below.
For mechanical systems that are not listed or items that are not explicitly defined, use appropriate tags that follow the same basic format.
Air System Terminal Units | Tag | Fan System # | Floor # | Sequential | Example | Notes
Supply Air Butterfly Terminals | SAT | 1 | B | 1 | SAT-1-B-1 | Supply Termainal Sequential Numbering can be different than Exhaust/Return.
Supply Air Venturi Air Valve | SAV | 1 | B | 1 | SAV-1-B-1
Return Air Butterfly Terminal | RAT | 2 | G | 2 | RAT-2-G-2
General Exhaust Butterfly Terminal | GET | 3 | 1 | 3 | GET-3-1-3
General Exhaust Venturi Air Valve | GEV | 4 | 2 | 4 | GEV-4-2-4
Fume Hood Exhaust Butterfly Terminal | FET | 5 | 3 | 5 | FET-5-3-5
Fume Hood Exhaust Venturi Air Valve | FEV | 5 | 3 | 5 | FEV-5-3-5 | Design standard is to use venturi valves for fume hoods.
Point Exhaust Butterfly Terminal | PET | 6 | 4 | 6 | PET-6-4-6
Point Exhaust Venturi Air Valve | PEV | 7 | 5 | 7 | PEV-7-5-7
Radiant Ceiling Panel assoc. w/Term | RCP | 1 | B | 1 | RCP-1-B-1 | Use tagging to match associated supply air terminal unit, i.e. this RCP would be associated with SAT-1-B-1
Fin Tube Radiation assoc. w/Term | FTR | 1 | B | 1 | FTR-1-B-1A | Use tagging to match associated supply air terminal unit. Use letters if multiple pieces of radiation controlled together.
Fin Tube Radiation Stand-alone | FTR |  |  | 8 | FTR-8 | Any radiation not associated with another terminal unit should be uniquely tagged.
Booster Humidifier | BH | 1 | B | 4 | BH-1-B-4 | Tagging should match associated supply air terminal unit, i.e. this BH would be associated with SAT-1-B-4
Miscellaneous Terminal Units | Tag | Fan System # | Floor # | Sequential | Example | Notes
Convector | CONV |  |  | 9 | CONV-9 | The ninth convector in the building.
Unit Heater | UH |  |  | 1 | UH-1 | The first unit heater in the building.
Cabinet Unit Heater | CUH |  |  | 2 | CUH-2 | The second cabinet unit heater in the building.
Fan Coil Unit | FCU | NA | NA | 3 | FCU-3 | Third fan coil unit in the building.
Booster Fan | BF | 1 | B | 4 | BF-1-B-4 | The fourth booster fan in the basement associated with fan system 1. This could be an AHU or exhaust system. Uncommon.
Main Mechanical Systems | Tag | System # | System Letter |  | Example | Notes
Hot Water Heat Exchangers | HX | 1 | A |  | HX-1A | The first heat exchanger in the first hot water system.
Chilled Water Heat Exchangers | CX | 2 | B |  | CX-2B | The second chilled water heat exchanger in the second chilled water system.
Chillers | CH | 3 | C |  | CH-3C | The third chiller in the third chiller system.
Air Handling Units | AHU | 4 | D |  | AHU-4D | The fourth AHU in the fourth AHU system.
Make Up Air Units | MUA | 5 |  |  | MUA-5 | The fifth MUA unit in the building. Typically 100% OA units for utilitarian applications.
Heat Recovery Units | HRU | 6 | B |  | HRU-6B | The second heat recovery unit in the sixth heat recovery system.
Roof Top Units | RTU | 7 |  |  | RTU-6 | The sixth roof top unit in the building.
Supply Fans | SF | 8 |  |  | SF-8 | Typically supply fans for ventilation. Number sequentially after AHU supply fans.
Exhaust Fans | EF |  |  | 2 | EF-2 | Typically general exhaust or ventilation. Number sequentially after EF system fans.
Relief Fans | RLF |  |  | 3 | RLF-3 | The third non-manifolded relief fan in the building.
Fans Within AHU Systems | Tag | System # | System Letter | Sequential | Example
Exhuast Fans | EF | 1 | A |  | EF-1A | The first exhaust fan in a manifolded system.
Supply Fans | SF | 2 | B | 3 | SF-2B-3 | The 3rd supply fan of AHU-2B.
Return Fans | RF | 2 | A | 2 | RF-2A-4 | The 2nd return fan for AHU-2A.
Relief Fans | RLF | 3 | B | 1 | RLF-3B-2 | The 1st relief fan of AHU-3B.
VFD's | VFD | 2 | B | 3/4 | VFD-SF-2B-3/4 | The VFD for supply fans 3 & 4 of AHU-2B
Smoke & Fire/Smoke Dampers | Tag | System # | Floor # | Sequential | Example | Notes
Supply Smoke Damper | SSD | 1 | 3 | 12 | SSD-1-3-12 | Systems, i.e. AHU-1A,B,C,D, would be shortend to 1
Return Smoke Damper | RSD | 1 | 3 | 13 | RSD-1-3-13
Exhaust Smoke Damper | ESD | 1 | 3 | 13 | ESD-1-3-13
Supply Fire/Smoke Damper | SFSD | 2 | 4 | 16 | SFSD-2-4-16
Return Fire/Smoke Damper | RFSD | 2 | 4 | 17 | RFSD-2-4-17
Exhaust Fire/Smoke Damper | EFSD | 2 | 4 | 17 | EFSD-2-4-17
Pumps | Tag | System # | System Letter |  | Example
Building Teriary Chilled Water Pumps | CHWP | 1 | A |  | CHWP-1A | The first chilled water pump of the first chilled water system where there is more than one pump piped in parallel.
Primary Chilled Water Pumps | PCHWP | 1 | B |  | PCHWP-1B | The second primary chilled water pump of the first chilled water system.
Secondary Chilled Water Pumps | SCHWP | 1 | C |  | SCHWP-1C | The third chilled water pump of the first chilled water system.
Process Chilled Water Pumps | PCP | 1 | B |  | PCP-1B | The second manifolded process chilled water pump of the first process chilled water system.
Condenser Water Pumps | CWP | 2 | B |  | CWP-2B | The second condenser water pump of the second chiller system.
Hot Water Pumps | HWP | 1 | B |  | HWP-1B | The second hot water pump of the first hot water system where there is more than one pump piped in parallel.
AHU HW Coil Circ Pumps | HWCP | 1 | B |  | HWCP-1B | The second AHU HW Circ Pump of redundant pumps for AHU-1 system.
Heat Recovery Pumps | HRP | 1 |  |  | HRP-1 | The heat recovery pump of the first heat recovery system without redundant pumps.
Condensate Pumps | CP | 1 | B |  | CP-1B | The second condensate pump of the first condensate receiver with duplex pumps.
VFD's | VFD | 1 | B |  | VFD-HWP-1B | The VFD for hot water pump HWP-1B.
Metering | Tag |  |  | Sequential | Example | Notes
Steam Flow Meter | SFM |  |  | 1 | SFM-1
Water Flow Meters | WFM |  |  | 2 | WFM-2 | Comprises all water meters - condensate, chilled water, hot water, etc.
Electrical Meter | EM |  |  | 3 | EM-3