**SECTION 22 14 00**

**FACILITY STORM DRAINAGE**

**BASED ON DFD MASTER SPECIFICATION DATED 4/6/18**

***This section has been written to cover most (but not all) situations that you will encounter. Depending on the requirements of your specific project, you may have to add material, delete items, or modify what is currently written. The Division of Facilities Development expects changes and comments from you.***

**P A R T 1 - G E N E R A L**

**SCOPE**

This section contains specifications for plumbing pipe and pipe fittings for this project. Included are the following topics:

PART 1 - GENERAL

 Scope

 Reference

 Reference Standards

 Shop Drawings

 Quality Assurance

 Delivery, Storage, and Handling

 Design Criteria

 Welder Qualifications

PART 2 - PRODUCTS

 Storm and Clear Water Waste

 Subsoil Drain

PART 3 - EXECUTION

 General

 Preparation

 Erection

 Copper Pipe Joints

 Welded Pipe Joints

 Threaded Pipe Joints

 Solvent Welded Pipe Joints

 Mechanical Hubless Pipe Connections

 Mechanical Joint Pipe Connections

 Push-On Gasketed Pipe Connections

 Mechanical Grooved Pipe Connections

 Mechanically Formed Tee Fittings

 Storm and Clearwater Waste and Vent

 Subsoil Drain

 Piping System Leak Tests

 Construction Verification Items

**RELATED WORK**

Section 01 91 01 or 01 91 02 – Commissioning Process

Section 22 08 00 – Commissioning of Plumbing

22 05 29 - Hangers and Supports for Plumbing Piping and Equipment

22 05 14 - Plumbing Specialties

**REFERENCE**

Applicable provisions of Division 1 govern work under this section.

**REFERENCE STANDARDS**

ANSI A21.4

ANSI A21.11

ANSI A21.51

ANSI B16.3 Malleable Iron Threaded Fittings

ANSI B16.4 Cast Iron Threaded Fittings

ANSI B16.5 Pipe Flanges and Flanged Fittings

ANSI B16.22 Wrought Copper and Wrought Copper Alloy Solder Joint Pressure Fittings

ANSI B16.29 Wrought Copper and Wrought Copper Alloy Solder Joint Drainage Fittings - DWV

ASTM A53 Pipe, Steel, Black and Hot-Dipped, Zinc Coated Welded and Seamless

ASTM A74 Cast Iron Soil Pipe and Fittings

ASTM A105 Forgings, Carbon Steel, for Piping Components

ASTM A126 Gray Cast Iron Castings for Valves, Flanges, and Pipe Fittings

ASTM A234 Pipe Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and Elevated Temperatures

ASTM A861 High Silicon Iron Pipe and Fittings

ASTM A888 Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste, and Vent

 Piping Applications

ASTM B32 Solder Metal

ASTM B88 Seamless Copper Water Tube

ASTM B306 Copper Drainage Tube (DWV)

ASTM B813 Liquid and Paste Fluxes for Soldering Applications of Copper and Copper Alloy Tube

ASTM C76 Reinforced Concrete Culvert, Storm Drain and Sanitary Pipe

ASTM C443 Joints for Circular Concrete Pipe Sewer and Culvert Pipe Using Rubber Gaskets

ASTM C564 Rubber Gaskets for Cast Iron Soil Pipe and Fittings

ASTM C1540 Heavy Duty Shielded Couplings for Joining Hubless Cast Iron Soil Pipe and Fittings

ASTM D1785 Poly Vinyl Chloride (PVC) Plastic Pipe

ASTM D2321 Underground Installation of Flexible Thermoplastic Sewer Pipe

ASTM D2241 Poly Vinyl Chloride (PVC) Pressure-Rated Pipe (SDR Series)

ASTM D2464 Threaded Poly Vinyl Chloride (PVC) Plastic Pipe Fittings, Schedule 80

ASTM D2466 Poly Vinyl Chloride (PVC) Plastic Pipe Fittings, Schedule 40

ASTM D2513 Thermoplastic Gas Pressure Pipe, Tubing, and Fittings

ASTM D2564 Solvent Cements for Poly Vinyl Chloride (PVC) Plastic Pipe and Fittings

ASTM D2657 Heat Fusion Joining of Polyolefin Pipe and Fittings

ASTM D2665 Poly Vinyl Chloride (PVC) Plastic Drain, Waste and Vent Pipe and Fittings

ASTM D2729 Poly Vinyl Chloride (PVC) Sewer Pipe and Fittings

ASTM D2774 Recommended Practice for Underground Installation of Thermoplastic Pressure Piping

ASTM D2855 Making Solvent Cemented Joints with Poly Vinyl Chloride (PVC) Pipe and Fittings

ASTM D3034 Type PSM Poly Vinyl Chloride (PVC) Sewer Pipe and Fittings

ASTM D3139 Joints for Plastic Pressure Pipes Using Flexible Elastomeric Seals

ASTM D3212 Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals

ASTM D3311 Drain, Waste and Vent (DWV) Plastic Fitting Patterns

ASTM F2618 CPVC Pipe and Fittings for Chemical Waste Drainage Systems

ASTM D4101 Propylene Plastic Injection and Extrusion Materials

ASTM F405 Corrugated Polyethylene (PE) Tubing and Fittings

ASTM F437 Threaded Chlorinated Poly Vinyl Chloride (CPVC) Plastic Pipe Fittings, Schedule 80

ASTM F438 Socket Type Chlorinated Poly Vinyl Chloride (CPVC) Plastic Pipe Fittings, Schedule 40

ASTM F441 Chlorinated Poly Vinyl Chloride (CPVC Plastic Pipe, Schedules 40 and 80

ASTM F656 Primers for Use in Solvent Cement Joints of Poly Vinyl Chloride (PVC) Plastic Pipe and

 Fittings

CISPI 301 Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste and

 Vent Piping Applications

CISPI 310 Couplings For Use In Connection With Hubless Cast Iron Soil Pipe And Fittings For

 Sanitary And Storm Drain, Waste And Vent Piping Applications

**SHOP DRAWINGS**

Schedule from the contractor indicating the ASTM, AWWA or CISPI specification number of the pipe being proposed along with its type and grade if known at the time of submittal, and sufficient information to indicate the type and rating of fittings for each service.

Statement from manufacturer on his letterhead that pipe furnished meets the ASTM, AWWA or CISPI specification contained in this section.

***Manufacturer's statement is appropriate on large or specialized projects and may be deleted on small projects.***

**QUALITY ASSURANCE**

Substitution of Materials: Refer to Section GC – General Conditions of the Contract, Equals and Substitutions.

Order all copper, cast iron, steel, PVC and polyethylene pipe with each length marked with the name or trademark of the manufacturer and type of pipe; with each shipping unit marked with the purchase order number, metal or alloy designation, temper, size, and name of supplier.

Any installed material not meeting the specification requirements must be replaced with material that meets these specifications without additional cost to the State.

**DELIVERY, STORAGE, AND HANDLING**

Promptly inspect shipments to ensure that the material is undamaged and complies with specifications.

Cover pipe to prevent corrosion or deterioration while allowing sufficient ventilation to avoid condensation. Do not store materials directly on grade. Protect pipe, tube, and fitting ends so they are not damaged. Where end caps are provided or specified, take precautions so the caps remain in place. Protect fittings, flanges, and unions by storage inside or by durable, waterproof, above ground packaging.

Offsite storage agreements will not relieve the contractor from using proper storage techniques.

Storage and protection methods must allow inspection to verify products.

**DESIGN CRITERIA**

Use only new material, free of defects, rust and scale, and meeting the latest revision of ASTM, AWWA or CISPI specifications as listed in this specification.

Construct all piping for the highest pressures and temperatures in the respective system.

Piping that is not in accordance with ASTM E-84/UL723 for flame spread of <25 and smoke development of <50 shall not be utilized in ventilation plenum spaces, including plenum ceilings.

Where weld fittings or mechanical grooved fittings are used, use only long radius elbows having a centerline radius of 1.5 pipe diameters.

Where ASTM A53 type F pipe is specified, grade A type E or S, or grade B type E or S may be substituted at Contractor's option. Where the grade or type is not specified, Contractor may choose from those commercially available.

Where ASTM B88, type L H (drawn) temper copper tubing is specified, ASTM B88, type K H (drawn) temper copper tubing may be substituted at Contractor's option.

**WELDER QUALIFICATIONS**

Welding procedures, welders, and welding operators for all building service piping to be in accordance with certified welding procedures of the National Certified Pipe Welding Bureau and Section 927.5 of ASME B31.9 Building Services Piping or AWS 10.9 Qualification of Welding Procedures and Welders for Piping and Tubing. Before any metallic welding is performed, Contractor to submit his Standard Welding Procedure Specification together with the Procedure Qualification Record as required by Section 927.6 of ASME B31.9 Building Services Piping.

***Welder certifications are required to be renewed every three years. If qualification papers are needed on a project, verify that they are current.***

Before any polyethylene fusion welding is performed, Contractor to submit certification that the welders to be used on this project have successfully demonstrated proper welding procedures in accordance with the Code of Federal Regulations, Title 49, Part 192, Section 192.285.

The Architect or Engineer reserves the right to test the work of any welder employed on the project, at the State's expense. If the work of the welder is found to be unsatisfactory, the welder shall be prevented from doing further welding on the project and all defective welds replaced.

**P A R T 2 - P R O D U C T S**

**STORM AND CLEARWATER WASTE and VENT**

Interior Above Ground:

Hubless cast iron soil pipe and fittings, ASTM A888; with no-hub couplings, CISPI 301, CISPI 310, ASTM A74. Pipe and fittings shall be marked with the collective trademark of the Cast Iron Pipe Institute. Cast iron piping and fittings shall be of A B & I Foundry, Charlotte Pipe and Foundry, or Tyler Pipe manufacturers.

Type M copper water tube, H (drawn) temper, ASTM B88; with cast copper drainage fittings (DWV), ANSI B16.23; wrought copper drainage fittings (DWV), ANSI B16.29; lead free (<.2%) solder, ASTM B32; flux, ASTM B813; copper phosphorous brazing alloy, AWS A5.8 BCuP.

Copper drainage tube (DWV), ASTM B306; with cast copper drainage fittings (DWV), ANSI B16.23; wrought copper drainage fittings (DWV), ANSI B16.29; lead free (<.2%) solder, ASTM B32; flux, ASTM B813; copper phosphorous brazing alloy, AWS A5.8 BCuP.

PVC plastic pipe, Schedule 40, Class 12454 (PVC 1120), ASTM D1785; PVC plastic drain, waste and vent pipe and fittings, ASTM D2665; fitting patterns, ASTM D3311; primer, ASTM F656; solvent cement, ASTM D2564.

***Above ground PVC should not be used where smoke generation, noise transmission or physical abuse/durability are an issue.***

CPVC plastic pipe, Schedule 40, ASTM D1784, Class 23447 Type IV, with drainage pattern fittings per ASTM D3311, Solvent cement joints utilizing one step primerless cement as approved by the manufacturer. All fittings and pipe shall be tested and listed in accordance with CAN/ULC S102.2 and tested in general accordance with ASTM E-84/UL723 for flame spread of <25 and smoke development of <50. CPVC pipe and fittings shall be of Charlotte Chem Drain or Spears Lab Waste manufacturers, or equal.

***CPVC material should be used for plenum areas or where high temperature (up to 220 degrees F) discharge are possible.***

Pressurized Interior Above Ground:

PVC Plastic pipe, Schedule 40, Class 12454, where temperature will not exceed 130 degrees F, ASTM D1784, ASTM D1785, with solvent cement joint fittings, pressure rated, ASTM D2466, medium or long sweep radius fittings; primer, ASTM F656; solvent cement, ASTM D2564.

***Schedule 80 and/or CPVC may be inserted if the application requires higher temperature or higher pressure rated material.***

Type L copper water tube, H (drawn) temper, ASTM B88; with cast copper drainage fittings (DWV), ANSI B16.23; wrought copper drainage fittings (DWV), ANSI B16.29; lead free (<.2%) solder, ASTM B32; flux, ASTM B813.

Galvanized steel pipe, Schedule 40, Type F, Grade A, ASTM A53; with cast iron threaded drainage fittings, ASTM B16.12.

Interior Below Ground 15" and Smaller:

Cast iron soil pipe and fittings, hub and spigot, service weight, CISPI 301, ASTM A74; ASTM A888 with neoprene rubber compression gaskets, ASTM C564 and CISPI HSN 85. Pipe and fittings shall be marked with the collective trademark of the Cast Iron Pipe Institute. Cast iron piping and fittings shall be of A B & I Foundry, Charlotte Pipe and Foundry, or Tyler Pipe manufacturers.

PVC plastic pipe, Schedule 40, Class 12454 (PVC 1120), ASTM D1785; PVC plastic drain, waste and vent pipe and fittings, ASTM D2665; fitting patterns, ASTM D3311; primer, ASTM F656; solvent cement, ASTM D2564.

***CPVC material should be copied and pasted from the above ground material section above for areas with high temperature discharge. Cast iron piping for underground systems should be avoided. Plastic material is preferred.***

Exterior Below Ground 10" and Smaller:

Non-reinforced concrete sewer, storm drain and culvert pipe, Class III, ASTM C14; rubber gasket joints, ASTM C443; bell and spigot or tongue and groove ends.

***Review installations below railways and highways to determine if higher Class IV or V piping is required.***

Exterior Below Ground 15" and Smaller:

Cast iron soil pipe and fittings, hub and spigot, service weight, CISPI 301, ASTM A74; ASTM A888 with neoprene compression rubber gaskets, ASTM C564 and CISPI HSN 85. Pipe and fittings shall be marked with the collective trademark of the Cast Iron Pipe Institute. Cast iron piping and fittings shall be of A B & I Foundry, Charlotte Pipe and Foundry, or Tyler Pipe manufacturers.

PVC plastic pipe, Schedule 40, Class 12454 (PVC 1120), ASTM D1785; PVC plastic drain, waste and vent pipe and fittings, ASTM D2665; fitting patterns, ASTM D3311; primer, ASTM F656; solvent cement, ASTM 2564.

Type PSM PVC sewer pipe and fittings, SDR 35, Class 12454-B (PVC 1120), ASTM D3034; primer, ASTM F656; solvent cement, ASTM 2564; or integral bell and flexible elastomeric seal, ASTM D3212.

Corrugated PVC pipe and fittings with smooth interior, ASTM F949; gasketed joint, ASTM D3212; elastomeric gasket, ASTM F477.

Corrugated polyethylene pipe with smooth interior and minimum pipe stiffness of 50 psi, ASTM F-405/ASTM F-667, AASHTO M-252/AASHTO M-294 Type S; PVC gasketed fittings, ASTM F1336; elastomeric gasket, ASTM F477.

Exterior Below Ground 12" and Larger:

Reinforced concrete culvert, storm drain and sewer pipe, Class III, ASTM C76; rubber gasket joints, ASTM C443; bell and spigot or tongue and groove ends.

Pressurized Below Ground 3" and Smaller:

PVC Plastic pipe, schedule 40, Class 12454, where temperature will not exceed 130 degrees F, ASTM D1784, ASTM D1785, with solvent cement joint fittings, pressure rated, ASTM D2466, medium or long sweep radius fittings; primer, ASTM F656; solvent cement, ASTM D2564.

***Schedule 80 and/or CPVC may be inserted if the application requires higher temperature or higher pressure rated material.***

Type K copper water tube, H (drawn) temper, ASTM B88; with cast copper drainage fittings (DWV), ANSI B16.23; wrought copper drainage fittings (DWV), ANSI B16.29; lead free (<.2%) solder, ASTM B32; flux, ASTM B813.

Pressurized Below Ground 3" and Larger:

Ductile iron pipe, mechanical or push on joint, thickness Class 52, AWWA C151; with standard thickness cement mortar lining, AWWA C104; ductile iron or gray iron mechanical joint cement mortar lined fittings, Class 250, AWWA C110; ductile iron mechanical joint compact fittings, Class 350, AWWA C153; rubber gasket joints with gasket lubricant, AWWA C111. Provide 8 mil tube or sheet polyethylene encasement of iron pipe and pipe fittings, AWWA C105.

PVC pressure pipe, DR 18, Class 150, AWWA C900; with integral bell and elastomeric gaskets, ASTM D3139. Fittings and fitting polyethylene encasement to be same as noted above for ductile iron.

**SUBSOIL DRAIN**

Corrugated polyethylene tubing and fittings, standard tubing, perforated, ASTM F405; with polypropylene fabric filter cover.

PVC sewer pipe and fittings, perforated, Class 12454-B (PVC 1120), ASTM D2729; primer, ASTM F656; solvent cement, ASTM 2564; with polypropylene fabric filter cover.

**P A R T 3 - E X E C U T I O N**

**GENERAL**

Install pipe and fittings in accordance with reference standards, manufacturers recommendations and recognized industry practices.

**PREPARATION**

Cut pipe ends square. Ream ends of piping to remove burrs. Clean scale and dirt from interior and exterior of each section of pipe and fitting prior to assembly.

**ERECTION**

Install all piping parallel to building walls and ceilings and at heights which do not obstruct any portion of a window, doorway, stairway, or passageway. Where interferences develop in the field, offset or reroute piping as required to clear such interferences. Coordinate locations of plumbing piping with piping, ductwork, conduit and equipment of other trades to allow sufficient clearances. In all cases, consult drawings for exact location of pipe spaces, ceiling heights, door and window openings, or other architectural details before installing piping.

Where copper or steel piping is embedded in masonry or concrete, provide protective sleeve covering of elastomeric pipe insulation.

Install underground warning tape 6"-12" below finished grade above all exterior below ground piping. Where existing underground warning tape is encountered, repair and replace.

Maintain piping in clean condition internally during construction.

Provide clearance for installation of insulation, access to valves and piping specialties.

Provide anchors, expansion joints, swing joints and/or expansion loops so that piping may expand and contract without damage to itself, equipment, or building.

Do not route piping through transformer vaults or above transformers, panelboards, or switchboards, including the required service space for this equipment, unless the piping is serving this equipment

***This requirement is based on NFPA 70, 384-4 and 450-47.***

Install all valves and piping specialties, including items furnished by others, as specified and/or detailed. Provide access to valves and specialties for maintenance. Make connections to all equipment, fixtures and systems installed by others where same requires the piping services indicated in this section.

**COPPER PIPE JOINTS**

Remove all slivers and burrs remaining from the cutting operation by reaming and filing both pipe surfaces. Clean fitting and tube with metal brush, emery cloth or sandpaper. Remove residue from the cleaning operation, apply flux and assemble joint to socket stop. Apply flame to fitting until solder melts when placed at joint. Remove flame and feed solder into joint until full penetration of cup and ring of solder appears. Wipe excess solder and flux from joint.

**WELDED PIPE JOINTS**

Make all welded joints by fusion welding in accordance with ASME Codes, ANSI B31, and State Codes where applicable. "Weldolets" and "Threadolets" may be used for branch takeoffs up to one-half (1/2) the diameter of the main.

**THREADED PIPE JOINTS**

Use a thread lubricant or teflon tape when making joints; no hard setting pipe thread cement or caulking will be allowed.

**SOLVENT WELDED PIPE JOINTS**

Install in accordance with ASTM D2855 "Making Solvent Cemented Joints With PVC Pipe and Fittings". Saw cut piping square and smooth. Tube cutters may be used if they are fitted with wheels designed for use with PVC/CPVC pipe that do not leave a raised bead on pipe exterior. Support and restrain pipe during cutting to prevent nicks and scratches. Bevel ends 10-15 degrees and deburr interior. Remove dust, drips, moisture, grease and other superfluous materials from pipe interior and exterior. Check dry fit of pipe and fittings. Reject materials which are out of round or do not fit within close tolerance. Use heavy body solvent cement for large diameter fittings.

Maintain pipe, fittings, primer and cement between 40 and 100 degrees during application and curing. Apply primer and solvent using separate daubers (3" and smaller piping only) or clean natural bristle brushes about 1/2 the size of the pipe diameter. Apply primer to the fitting socket and pipe surface with a scrubbing motion. Check for penetration and reapply as needed to dissolve surface to a depth of 4-5 thousandths. Apply solvent cement to the fitting socket and pipe in an amount greater than needed to fill any gap. While both surfaces are wet, insert pipe into socket fitting with a quarter turn to the bottom of the socket. Solvent cement application and insertion must be completed in less than 1 minute. Minimum of 2 installers is required on piping 4" and larger. Hold joint for 30 seconds or until set. Reference manufacturers recommendations for initial set time before handling and for full curing time before pressure testing. Cold weather solvent/cement may be utilized only under unusual circumstances and when specifically approved by the **DFD** Project Representative.

**MECHANICAL HUBLESS PIPE CONNECTIONS**

Place the gasket on the end of one pipe or fitting and the clamp assembly on the end of the other pipe or fitting. Firmly seat the pipe or fitting ends against the integrally molded shoulder inside the neoprene gasket. Slide the clamp assembly into position over the gasket. Tighten fasteners to manufacturers recommended torque.

**MECHANICAL JOINT PIPE CONNECTIONS**

Comply with AWWA C600/C605 installation requirements. Clean pipe end and socket. Clean and lubricate pipe end, socket and gasket with soapy water or gasket lubricant. Place gland and gasket, properly oriented, on pipe end. Insert pipe end fully into socket and press gasket evenly into recess keeping joint straight. Press gland evenly against gasket, insert bolts and hand tighten nuts. Make joint deflection prior to tightening bolts. Evenly tighten bolts in sequence to recommended torque.

**PUSH-ON GASKETED PIPE CONNECTIONS**

Clean pipe end, bell, gasket seat and gasket of dirt or debris. Coat end of pipe and gasket with gasket lubricant. Insure pipe is supported off the ground so lubricant does not pick up dirt. Push spigot end into gasket bell with levered pipe joining tool recommended by pipe manufacturer. Large diameter exterior mains may be joined by pushing end of pipe section with backhoe against wood blocking over pipe end. Insert to fully seated position or to reference mark on pipe.

**MECHANICAL GROOVED PIPE CONNECTIONS**

Use pipe factory grooved in accordance with the coupling manufacturer's specifications or field grooved pipe in accordance with the same specifications using specially designed tools specially designed for the application. Lubricate pipe and coupling gasket, align pipe, and secure joint in accordance with the coupling manufacturer's specifications.

**STORM AND CLEARWATER WASTE and VENT**

Verify invert elevations and building elevations prior to installation. Install exterior piping pitched to drain at indicated elevations and slope. Install interior piping pitched to drain at minimum slope of 1/8" per foot where possible and in no case less than 1/16" per foot for piping 3" and larger.

Install exterior piping below predicted frost level and not less than 5' bury depth to top of pipe wherever possible. Where piping is located above predicted frost level, provide frost protection in accordance with SPS 382.30(11)(c).

**SUBSOIL DRAIN**

Verify invert elevations and building elevations prior to installation. Install piping sloped to drain to locations indicated. Where subsoil drains are required to penetrate foundation work, sleeve subsoil drains or use nonperforated sections of piping and place prior to foundation work.

Secure joints and piping where corrugated polyethylene is used to prevent movement during laying and backfill. Route piping in straight lines. Plug dead ends of pipe with pipe caps or concrete plugs. Extend filter fabric cover over all piping and fittings with fabric cover joints overlapping and banded.

Bed piping on and backfill around subsoil drains with pea gravel or No. 2 coarse aggregate (DOT 501.3.6.4.5) to a level 12" above or as indicated.

***Where soil contains excessive fines, specify geotextile fabric wrap placed in trench around granular backfill.***

**PIPING SYSTEM LEAK TESTS**

Isolate or remove components from system which are not rated for test pressure. Perform final testing for medical and lab gas with all system components in place. Test piping in sections or entire system as required by sequence of construction. Do not insulate or conceal pipe until it has been successfully tested.

If required for the additional pressure load under test, provide temporary restraints at fittings or expansion joints. Backfill underground water mains prior to testing with the exception of thrust restrained valves which may be exposed to isolate potential leaks.

For hydrostatic tests, use clean water and remove all air from the piping being tested by means of air vents or loosening of flanges/unions. Measure and record test pressure at the high point in the system.

For air or nitrogen tests, gradually increase the pressure to not more than one half of the test pressure; then increase the pressure in steps of approximately one-tenth of the test pressure until the required test pressure is reached. Examine all joints and connections with a soap bubble solution or equivalent method. System will not be approved until it can be demonstrated that there is no measurable loss of test pressure during the test period.

Inspect system for leaks. Where leaks occur, repair the area with new materials and repeat the test; caulking will not be acceptable.

Entire test must be witnessed by the Division's representative. All pressure tests are to be documented on **Division of Facilities Development** forms to be provided to the contractor.

 Test Initial Test Final Test

## System Medium Pressure Duration Pressure Duration

Clearwater Waste and Vent Water N/A 10' water 2 hr

Storm and Clearwater Waste Water N/A 10' water 2 hr

Pressurized Storm/Clearwater Waste Water N/A 100 psig 2 hr

# CONSTRUCTION VERIFICATION ITEMS

Contractor is responsible for utilizing the construction verification checklists supplied under specification Section 2208 00 in accordance with the procedures defined for construction verification in Section 01 91 01 or 01 91 02.

END OF SECTION