SECTION 07 61 13.01

DOUBLE LOCKING VERTICAL LEG SHEET METAL ROOFING SYSTEM:

NON-STRUCTURAL STEEL

BASED ON DFD MASTER SPECIFICATION DATED (03/12/2026)

(Notes to A/E: All notes and information screen viewable in bold red text within (Parentheses) are directions for the Architect/Engineer's use in document preparation only and should not be reprinted in the specifications. System options are identified within [brackets] in red type. This language SHALL be edited to meet the exact scope of the project. Remove brackets from selected option and change text to black. DO NOT USE RED TEXT.

This section has been written to cover the installation of Double Locking Vertical Leg Sheet Metal Roofing Systems (DLVLSMRS) over an insulated deck substrate or uninsulated deck substrate. The Double Locking Vertical Leg Sheet Metal Roofing System specified in this Section shall be installed over a solid substrate with a minimum slope of 3-inches in 12-inches (3":12").

If a vented deck substrate is required, specify the substrate assembly using the following sections: Section 07 22 16.10 - Nailbase Insulation Panels, in tandem with Section 06 10 53.01 - Miscellaneous Rough Carpentry – Roofing. Refer to DFD’s Design Guidelines for Roofing for the ventilation requirements under a Double Locking Vertical Leg Sheet Metal Roofing System.

Depending on the requirements of your specific project, you may have to add material, delete items, or modify what is currently written. The Division of Facilities Development (DFD) expects changes and comments from you.

IN THE DRAWING SET

Plan, elevation, and detail sheets, are required for all Double Locking Vertical Leg Sheet Metal Roofing Systems. The A/E is required to calculate, key, and depict the uplift pressures and zones for the system on the plan sheets.

The A/E is required to add the note listed below to all plan, elevation, or detail sheets that include Double Locking Vertical Leg Sheet Metal Roofing System scope:

All Double Locking Vertical Leg Sheet Metal Roofing Systems installed on DFD projects require validation of the wind uplift performance standards listed herein, for the complete system and all system attachment components integral to wind uplift rating, via documentation of stamped engineering and assembly testing.

NOTE: ALL DOUBLE LOCKING VERTICAL LEG SHEET METAL ROOFING SYSTEMS THAT DO NOT HAVE STAMPED ENGINEERING AND TESTING DOCUEMNTATION FOR WIND UPLIFT PERFOMRANCE SUBMITTED FOR VALIDATION AS A PART OF THE SUBMITTAL PROCESS, SHALL BE REJECTED.)

PART 1 – GENERAL

SCOPE

This section consists of providing all labor, material, equipment, and supervision necessary to provide a weather and watertight vertical leg, mechanically seamed metal panel roof system complete, in place, as shown on the drawings and specified herein.

PART 1 – GENERAL

Scope

Related Sections

Reference Standards

Definitions

Guarantee / Warranty

State of Wisconsin Guarantee

Metal Panel Manufacturer’s Weathertight Warranty

Metal Panel Manufacturer’s Limited Paint Finish Warranty

Quality Assurance

Work Sequence

Job Conditions

Delivery, Storage, and Handling

Submittals

Samples

Mockups

Installation Meetings

PART 2 – PRODUCTS

Performance Requirements

Manufacturers and Materials

Double Locking Vertical Leg Sheet Metal Roof Panel

Trim Metal and Flashing Metal

Roof Panel Attachment Clips

Ice & Water Protection Membrane

Synthetic Underlayment

Cap Nails

Thermal Barrier

Insulation

Cover Board

Ridge Ventilation

Snow Retention System

Accessory Mounting System

Miscellaneous

PART 3 – EXECUTION

Examination

Site Conditions

Substrate Preparation

Installation of Thermal Barrier

Installation of Insulation System

Installation of Cover Board

Installation of Ice & Water Protection Membrane

Installation of Synthetic Underlayment

Installation of Double Locking Vertical Leg Metal Roof Panels

Installation of Roof Flashing with Panel Termination

Roof Edge Flashing

Panel Termination at Sidewall

Panel Termination at Head Wall / High Side

Zee Closure

Sidewall Flashing

Head Wall / High Side Flashing

Hip / Ridge Cap Flashing

Valley Flashing

Roof Flashing at Curbs

Saddle / Cricket Flashing

Pipe Flashing

Expansion Joint Flashing

Counter Flashing

Saddle / Cricket Flashing

Installation of Ridge Ventilation Flashing

Installation of Vented Ridge Cap

Installation of Vented Zee Closure for Ridge Vent Openings

Installation of Miscellaneous Roof Flashing

Workmanship

Cleaning

RELATED SECTIONS

(Note to A/E: review all scope of work and determine other related sections, which impacts this section, or work that is impacted by this section. A/E to add or remove sections below and otherwise, as needed.

Soffit, gutter, downspout, and other metal elements that ARE NOT integral to DLVLSMRS (including fascia or coping), shall be specified within Section 07 63 00 Sheet Metal Roofing Specialties. NOTE: Fascia or coping elements that ARE integral to the DLVLSMRS shall be specified within this work section.

Include section 26 41 13.14 for Lightning Protection Systems that must be removed, altered, interrupted, or disabled to perform work.)

[06 10 53.01 – Miscellaneous Rough Carpentry – Roofing]

[07 05 00 – Common Work Results for Thermal and Moisture Protection]

[07 05 05 – Selective Demolition for Thermal and Moisture Protection]

[07 22 16 – Ventilated Nail Base Insulation – [Premanufactured Units] [Field Fabricated Units]

[07 63 00 – ​Sheet Metal Roofing Specialties]

[26 41 13.14 – Lightning Protection for Buildings – Roof Level Upgrade]

Reference STANDARDS

AISI – American Iron and Steel Institute, current edition.

ANSI FM 4474 – American National Standard for Evaluating the Simulated Wind Uplift Resistance of Roof Assemblies Using Static Positive and/or Negative Differential Pressures; 2010.

ANSI/SPRI FX-1 – Standard Test Procedure for Determining the Withdrawal Resistance of Roofing Fasteners, or equivalent test procedure; 2021.

ASCE/SEI 7 – Minimum Design Loads and Associated Criteria for Buildings and Other Structure; 2016.

ASTM A653/A653M – Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy Coated (Galvanized) by the Hot-Dip Process; 2025.

ASTM A1011 – Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength; 2018.

ASTM C920 – Standard Specification for Joint Sealants; 2024.

ASTM C1513 – Standard Specification for Steel Tapping Screws for Cold-Formed Steel Framing Connections; 2024.

[ASTM C1177 – Standard Specification for Glass Mat Gypsum Substrate for use as Sheathing: 2017.]

[ASTM C1289 – Faced Rigid Cellular Polyisocyanurate Thermal Insulation Board; 2025.]

[ASTM D1056 –Specification for Flexible Cellular Materials; 2020.]

ASTM D2244 – Standard Practice for Calculation of Color Differences from Instrumentally Measured Color Coordinates; 2025.

ASTM D1970/D1970M – Standard Specification for Self-Adhering Polymer Modified Bituminous Sheet Materials Used as Steep Roofing Underlayment for Ice Dam Protection; 2021.

ASTM D4214 – Test Methods for Evaluating Degree of Chalking of Exterior Paint Films; 2023.

ASTM D6294 – Standard Test Method for Corrosion Resistance of Ferrous Metal Fastener Assemblies Used in Roofing and Waterproofing; 2024.

ASTM D4214 – Standard Test Method for Evaluating Degree of Blistering of Paints; 2017.

ASTM E108 – Standard Test Methods for Fire Tests of Roof Coverings; 2020(a).

ASTM E283 – Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Skylights, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen; 2019.

ASTM E331 – Standard Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference; 2023.

ASTM E1592 – Standard Test Method for Structural Performance of Sheet Metal Roof and Siding Systems by Uniform Static Air Pressure Difference; 2017.

ASTM E1646 – Standard Test Method for Water Penetration of Exterior Metal Roof Panel Systems by Uniform Static Air Pressure Difference; 2024.

ASTM E1680 – Standard Test Method for Rate of Air Leakage Through Exterior Metal Roof Panel Systems; 2022.

ASTM E2140 – Standard Test Method for Water Penetration of Metal Roof Panel Systems by Static Water Pressure Head; 2023.

ASTM F1667 – Standard Specification for Driven Fasteners: Nails, Spikes, and Staples; 2021.

ASTM F1941 – Standard Specification for Electrodeposited Coatings on Mechanical Fasteners; 2025.

Department of Defense (DoD) Unified Facilities Criteria (UFC) – Roofing Design Criteria; 2020.

Factory Mutual (FM) 4471 – Approval Standard for Class 1 Panel Roofs; 2010.

International Building Code (IBC) – Current addition adopted by the State of Wisconsin.

International Energy Conservation Code (IECC) – Current addition adopted by the State of Wisconsin.

NRCA – Guidelines for Rooftop-mounted Photovoltaic Systems, Second Edition, 2018

NRCA – Roofing and Waterproofing Manual, 2023.

SMACNA – Architectural Sheet Metal Manual, 2012.

UL 263 – Standard for Fire Tests of Building Construction and Materials; 2025.

UL 580 (Class 90) – Standard for Safety Tests for Uplift Resistance of Roof Assemblies; 2024.

UL 790 – Fire Hazard Classifications, A, B, C; 2022.

UL 1897 – Standard for Safety, Uplift Tests for Roof Covering Systems; 2023.

UL 2218 – Standard for Impact Resistance of Prepared Roof Covering Materials; 2024.

DEFINITIONS

Manufacturer

Manufacturers are defined as the supplier and fabricator of the roofing system and its components, holding the warranty and testing data required for verification of design performance.

Contractor Manufacturer:

Contractor manufacturers are defined as the fabricator of components of the roofing system, using a combination of site fabricated components, manufacturer components, and holding the warranty and testing data required for verification of design performance.

Roof Assembly:

A system designed to provide weather protection and resistance to design loads. The system consists of a roof covering and roof deck or a single component serving as both the roof covering and the roof deck. A roof assembly can include an underlayment, a thermal barrier, insulation, and/or a vapor retarder.

Roof Covering:

The covering applied for weather resistance, fire classification, or appearance.

Roof Deck:

The flat or sloped surface constructed on top of the exterior walls of a building or other supports for the purpose of enclosing the story below, or sheltering an area, to protect it from the elements, not including its supporting members or vertical supports.

Roof System:

A system designed to be weatherproof and improve building thermal resistance. A roof system consists of a roof covering and other interacting roofing components and may include a vapor retarder, thermal barrier, insulation or other similar substrate. The system does not include the roof deck unless it is part of a single component serving as the roof covering and the roof deck.

Roof Ventilation:

The natural or mechanical process of supplying conditioned or non-conditioned air to, or removing such air from, attics, cathedral ceilings or other enclosed spaces over which a roof assembly is installed.

SME:

Subject Matter Expert. Division of Facility Development’s (DFD) designated expert concerning technical matters specific to building envelope / roofing.

Roofing System Contractor:

The Manufacturer’s approved and authorized Contractor installing the Roof System components and assemblies that are included in the Metal Panel System Warranty.

Guarantee / Warranty

The following information shall be included on all guarantee and warranty documents:

State of Wisconsin Agency, city or township, street address where work is performed, building name, DFD project number, all roof areas involved (denoted by letter or number) as indicated on the drawings, and total square footage of all roof areas involved in the scope of Work.

The Contractors Performance-Payment Bond is only required to apply to this trade section during the construction period and the first year of the guarantee period. Said Bond shall not apply to any extended guarantee period beyond the first year. Such extended guarantees are limited to the applicable Contractor and Manufacturer as herein specified.

State of Wisconsin Guarantee:

(Note to A/E: Insert the State of Wisconsin Guarantee in the project documents, following any testing inserts included at the end of this section.)

State of Wisconsin Roof System Guarantee: Provide five (5) year written guarantee that warranties all roofing and flashing furnished under the Contract, is watertight and free from defects in materials and workmanship for the duration, as stipulated in the contract-required guarantee form.

The Roofing System Contractor and General Prime Contractor (GPC) shall perform a minimum of two (2) roof system inspections during the term of this guarantee. The first inspection shall be approximately two (2) years after the installation date; the second and final inspection shall be performed within the last six (6) months of the five (5) year guarantee. The Roofing System Contractor and GPC shall contact the Agency contact to arrange for a site visit date. If available, the Agency contact shall accompany the Contractor(s) during the inspection. The Roofing System Contractor in conjunction with the GPC shall submit written inspection reports by e-mail to the DFD SME and Agency Representative within 5 working days after the inspection is performed, and prior to the expiration date of the guarantee.

A copy of the required State of Wisconsin Roof System 5-yr Guarantee form is located at the end of this Section and may also be acquired electronically at: https://doa.wi.gov/Pages/DoingBusiness/MasterSpec_Div7.aspx

The General Prime Contractor and all sub-contractors shall review the guarantee and requirements of this section prior to submitting a Bid for all work.

Manufacturer’s / Contractor Manufacturer’s Weathertight Warranty:

The following information shall be included on all guarantee and warranty documents:

State of Wisconsin (Owner), Agency, city or township, street address where work was performed, building name, Owner Project number, Owner (DOA) building number, all roof areas involved and total sq. ft. area of all roof areas.

Include and provide all product(s), labor and installation methods necessary and as specified herein, including manufacturer requirements not found specified herein, as required by the Manufacturer / Contractor Manufacturer to obtain the specified warranty requested herein.

Existing re-installed and new metal flashing and new wood blocking mechanical securement shall be covered in the State guarantee but not the Manufacturer / Contractor Manufacturer system warranty specified herein.

(Note to A/E: Select length of Manufacturer’s / Contractor Manufacturer warranty wind speed coverage. Systems specified with a warranty wind speed coverage above 55 mph require additional attachment and detail considerations.)

Provide the metal panel Manufacturer / Contractor Manufacturer NDL (“No-Dollar-Limit”) “Total System” warranty covering defects in workmanship, materials and all associated roof system components supplied by the Manufacturer / Contractor Manufacturer for a period of twenty (20) years with a wind speed coverage of [120] [150] miles per hour from the date of substantial completion of the roof.

All new roof system components, including, but not limited to insulation, Contractor Manufacturer fabricated metal flashing, pre-molded products, fasteners, adhesive, sealants, and accessories, shall be covered by the Manufacturer NDL (“No-Dollar-Limit”) / “Total System” warranty specified herein.

Manufacturer’s Limited Paint Finish Warranty:

Provide the Manufacturer’s thirty-five (35) year limited standard color paint finish warranty to meet the following quality standards: Will not chalk in excess of an 8 rating per ASTM D-4214. Will not fade in excess of a 5 rating, per ASTM D-2244-02. Will not lose adhesion.

Quality Assurance

The Roofing System Contractor is required to be recognized by the Manufacturer, as an approved and authorized applicator of the roofing system and all associated products, components, and assemblies specified herein.

The Roofing System Contractor shall follow the Manufacturer’s current written instructions regarding application and storage, except where it is superseded by more stringent requirements specified herein.

If the Manufacturer / Contractor Manufacturer requires improvements to the system materials and / or techniques specified herein, in order to obtain guarantees / warranties, the Roofing System Contractor shall then make a written request to the A/E and DFD representative stating the nature of the proposed changes, and that if approved, will be accomplished at no additional cost to contract.

The Roofing System Contractor shall schedule an onsite installation meeting with the GPC, the DFD’s Project Representative and the A/E. The meeting shall occur within the first two (2) days of the start of Roofing System construction. The purpose of the meeting is for the A/E to review and document scope of project and installation procedures with the Contractor.

The Roofing System Contractor is required to have been in business for a minimum of three (3) years, and within the past three (3) years, the Roofing System Contractor shall be able to document the successful completion of a minimum of three (3) projects of similar size and/or scope as compared to the work as specified in this Section. Backup documentation / verification shall be a submittal requirement.

All system components required by the Manufacturer / Contractor Manufacturer, included in construction documents or otherwise, shall be provided and installed by the Contractor to achieve the Manufacturer / Contractor Manufacturer warranty. Any components required by the Manufacturer / Contractor Manufacturer, that are not specified in construction documents, require written approval by the A/E prior to installation, and be required as part of the submittal package. System components listed in the construction documents but not otherwise warranted by the Manufacturer / Contractor Manufacturer, shall be upgraded to achieve Manufacturer / Contractor Manufacturer warranty at time of bid, if not listed herein. Components installed that do not meet the above-listed criteria shall be cause for rejection of the work.

The Roofing System Contractor shall provide all equipment that is recommended by the Manufacturer and the standards agencies listed herein, that is required for the proper installation of the materials specified.

The Roofing System Contractor shall take multiple digital photos daily and throughout the duration of the project. All photos shall be identified by the roof area where the photos are taken.

Required photographic documentation types include, but are not limited to:

- existing conditions

- various stages of demolition

- the entire installation starting at the roof deck and continuing throughout all roof system layers, various metal flashing details, transitions, penetrations, penetration height changes, over-all views of the field, drains and scuppers, all roof areas in difficult watertight locations, and mechanical fastening that is hidden from view, or otherwise concealed beneath the completed work

- completed work

WORK SEQUENCE

Sequence all work with the other work of the contract, so as not to necessitate construction traffic from this or other trades over unprotected roof assembly surfaces.

All work listed in this section shall be coordinated with the installation of associated envelope, air and/or vapor barriers, screening, masonry, sheet metal, roofing, waterproofing, flashings, roof accessories, MEP, photovoltaic work, and work specified under other sections, as the work of this section proceeds.

Sequence the work to prevent any unnecessary deterioration of installed roofing assembly elements (new or existing to remain in place). Damage by use of roof assemblies for storage and walking surface, or equipment traffic, shall be replaced at no cost to DFD.

Job Conditions

The GPC shall maintain at the jobsite at least one (1) copy of the latest version of the Manufacturer’s installation manual / handbook, including details and technical information concerning application techniques, for all primary roofing system materials required by the work. The GPC shall also maintain at least one (1) copy each of the construction set specification and drawings, Request for Information (RFI), Construction Bulletin (CB), and Change Order (CO) documents, and all other approved signed submittals throughout construction. Documents shall be stored and readily accessible to the Roofing System installation crews.

The Roofing System Contractor shall maintain, at the jobsite, at least one physically accessible copy of the Safety Data Sheets (SDS) manual, for all Roofing System materials used on this project or stored on the jobsite.

Upon commencement of the Work listed herein, and throughout the duration of the project, the building will be subject to leakage – as such, it shall be in a state of emergency when weather threatens. The existing building shall be protected by the Contractor from moisture entry (bulk water) and condensation (water vapor) caused by the Work listed herein (even in unforeseen weather conditions), for the duration of the project. The GPC shall be responsible for all damage to property due to moisture of any kind.

An effective watertight seal between existing roofing and new roofing is required at the end of each day's work. Temporary seals shall be removed upon installation of new permanent work.

Load roofing debris directly into trucks by means of approved chutes or other controlled means. All such gravel, rubbish, debris, etc. shall be removed from the site and disposed of by the GPC. All debris / material shall be controlled to prevent uncontrolled exiting from roof level. All debris shall be picked up continuously to prevent straying. Limit the number of locations where trucks may be loaded to avoid damage to property. The GPC shall be responsible for all damage to property. Throwing or dropping shall not be permitted.

Delivery, Storage, and Handling

The Roofing System Contractor shall make no deliveries to the project site, until a storage area has been identified for the project, and the DFD’s Project Representative and the user Agency Representative has approved onsite deliveries. The State shall not accept delivery, nor shall the State be responsible for any materials or equipment stored on the premises.

Deliver materials in original unopened containers of packaging clearly labeled with Manufacturer’s name, brand name, instructions for use, all identifying numbers and U.L. labels. Labels shall be maintained throughout the duration of the project.

Materials used on the job shall be stored in such a manner as not to create a nuisance or hazard.

Materials shall be stored on clean, raised platforms, with breathable, weather protective covering when stored outdoors. The Roofing System Contractor shall provide continuous protection from all materials against UV damage, exposure to moisture, and general weathering.

Store and handle all materials in a manner which does not damage the material. Materials contaminated with any foreign substance shall constitute damage. All damaged materials shall not be considered suitable for installation and shall be rejected and removed from the jobsite.

Adhesives, primers, coatings, sealants, and similar materials shall be stored in compliance with the temperature set by the Manufacturer of that specific product.

Store flammable products away from any ignition source – sparks, open flame, etc.

Select and operate material handling equipment that allows for the safe storage of materials. The Roofing System Contractor shall replace or make good any damage, loss, or injury caused by the improper use of material handling equipment. Do not use material handling equipment in a manner which overloads any portion of the building.

Storage of materials on completed work or within the building is prohibited.

Shrink wrap is not considered an acceptable weather protective covering. Ventilation cuts shall be made to all shrink-wrapped materials to allow for exhaust of moisture. All materials shall subsequently be covered with weather protective covering after the ventilation process. Materials damaged in the ventilation process shall be considered unsuitable for installation and shall be rejected

Submittals

(Note to A/E: Add or remove sections red bracketed as needed. Fastener pull testing insert ANSI/SPRI FX-1 shall be inserted into the specification documents consecutively following the end of this section.)

All Double Locking Vertical Leg Sheet Metal Roofing Systems installed on DFD projects require validation of the wind uplift performance standards listed herein, for the complete system and all system attachment components integral to wind uplift rating, via documentation of stamped engineering and assembly testing.

NOTE: ALL DOUBLE LOCKING VERTICAL LEG SHEET METAL ROOFING SYSTEMS THAT DO NOT HAVE STAMPED ENGINEERING AND TESTING DOCUEMNTATION FOR WIND UPLIFT PERFOMRANCE SUBMITTED FOR VALIDATION AS A PART OF THE SUBMITTAL PROCESS, SHALL BE REJECTED.

All submittals shall be in electronic format. The GPC shall upload accepted submittals into DFD’s Project Management Information System (PMIS). Prior to the start of Roofing System work, electronically submit to the A/E for review and acceptance. The following submittals as required herein:

The Manufacturer / Contractor Manufacturer “Assembly Letter” listing all the major materials to be used in the system, including but not limited to: panel material with all specifications, panel clip assemblies with all specifications, miscellaneous components with all specifications, method and spacing specification, UL Assembly Classification, and Manufacturer / Contractor Manufacturer sample warranty indicating length and type of warranty; Note: Sample warranty shall be removed and replaced with the active warranty upon in-service date activation.

The Manufacturer / Contractor Manufacturer letter stating the Roofing System Contractor is an approved and authorized applicator of the specified Roof System and all associated products and components. Note: If the Contractor Manufacturer is field fabricating the roof system by roll forming on-site, they shall provide a letter from the materials Manufacturer stating the Contractor Manufacturer and equipment they are using, is approved for on-site roll forming of the panels.

The Manufacturer / Contractor Manufacturer color chart. Provide actual color samples if requested.

The Manufacturer / Contractor Manufacturer current product data sheets for supplied products with specific product size / thickness noted.

The list of all the materials proposed for use on the project (including all non-system materials), starting at the roof deck and identified by the Manufacturer's name, size, thickness, type or grade, and rating. The list shall be submitted on Roofing System Contractor's letterhead stationery. The Roofing System Contractor shall verify that none of the materials submitted contain asbestos and state the following at the bottom of the material list submittal: “New products installed on this project do not contain asbestos”.

The Manufacturer / Contractor Manufacturer shop drawings showing the complete system assembly, all attachment components, and all other criteria listed below; The shop drawing set is required to be stamped by a Professional Engineer, acquired by the Manufacturer / Contractor Manufacturer.

Shop Drawing Requirements:

- Roof plans, elevations, and sections, including details of connections to adjoining work.

- Material type, thickness, weight, and finish.

- System details for material profile, forming, seams, and dimensions.

- Attachment details for joining, supporting, and securing the system, including termination points.

- Attachment details for layout and spacing of fasteners, cleats, clips, and all other attachments.

- Parameters for pullout strength of fasteners requisite for system and warranty requirements.

- Flashing details for all penetrations, flashings, counter-flashings, and expansion joint covers.

- Details of edge and transition conditions, including eaves, ridges, valleys, rakes, and crickets

- Panel installation layout with fixed points, expansion joints, and directions of thermal movement.

- [Attachment details for layout of bearing plates (spacing and placement) and attachment.]

- [Attachment details for layout of insulation and mechanical fastener attachment.]

The Manufacturer / Contractor Manufacturer shop drawings showing any proposed detail / specification changes as required to obtain the specified warranty.

Mechanical fastener pull testing results using test procedure ANSI/SPRI FX-1 2021; Standard Test Procedure for Determining the Withdrawal Resistance of Roofing Fasteners, or equivalent test procedure.

The Manufacturer / Contractor Manufacturer most current version of installation and detail manual edited to include only the system being installed, including: all trim, edging, flashing, closure, termination, hip / ridge assembly, and ventilation details being performed as a part of the roof system.

The Manufacturer / Contractor Manufacturer certification that the Roofing System Contractor has received training and is certified by the Manufacturer / Contractor Manufacturer to install specified products.

Roofing System Contractors Project Specific Quality Assurance Plan, at a minimum the plan shall include:

- Project name, address, number, manufacturer and subcontractor(s)

- Project scope and approach to project

- Emergency contact information

- Project Quality Assurance Manager name (Office) and job title

- Project Quality Control Manager name (On-site) and job title

- Project initiation inspections (including manufacturer)

- Project personnel and certifications

- Inspections and tests to be performed, by whom and when

- Control of nonconformance items to protect the quality of the installation

- Project completion inspections (including manufacturer)

The GPC shall submit in DFD’s Project Management Software Information System (PMIS), a Site-Specific Safety Report at the Pre-Construction meeting (reference General Conditions, Article 15). The report shall describe in detail the Roofing System Contractor’s implementation of specific OSHA regulations, worker safety program methods / means, roof perimeter safety and identification of the watch person required at all roof levels. Identify fire extinguishers and their locations, all equipment / operators on roof / ground in setup / storage area and travel routes used while performing the work.

(Note to A/E: When removing any portion of an existing roofing system, insert the following paragraph(s).)

[The Roofing System Contractor is responsible for all Category I Non-Friable Asbestos Containing Material (ACM) disturbed within the roof assembly during any and / all facets of this project. The Roofing System Contractor shall submit electronic copies of test results including a drawing indicating locations where test samples are taken. The Roofing System Contractor is required to take a minimum of two (2) samples of existing roof system(s) components encountered starting at the roof deck including existing vapor retarder, to be sent to an accredited testing lab. Take one (1) sample at the base flashing and one (1) sample from the field of the roof. Additional samples are required where roof areas are not of the same roof system or installation period. Each test result shall properly identify the DFD project number, project location, building name, building number & roof area / location where the test sample was taken. Laboratory fees and associated removal and disposal charges shall be the responsibility of the Roofing System Contractor, at no additional cost to the project.

The samples must be collected by an Asbestos Inspector or Exterior Asbestos Supervisor with current accreditation as required by DHS 159. The Roofing System Contractor shall have certified staff or hire an accredited third-party consultant, at no additional cost to the project.

Any disturbance to asbestos materials or assumed asbestos materials must be conducted by workers properly trained and currently certified in accordance with DHS 159. Laboratory results must be submitted prior to the start of Work.

Note: POSITIVE RESULTS

The Roofing System Contractor shall submit an electronic copy of the necessary regulatory notification for asbestos removal or an electronic copy of test results indicating the roofing materials intended for removal do not contain asbestos. (Refer to General Requirements Article “HAZARDOUS SUBSTANCES – ASBESTOS, LEAD AND POLYCHLORINATED BIPHENYLS (PCB’S)” for additional information.)]

At project completion, the Roofing system contractor shall submit documentation that they have performed an in-person Owner training regarding care of the roof system and associated warranties. The training shall consist of a page turn that reviews the Manufacturer’s Owner’s Manual, the warranty, and the Contractor 5-year guaranty. Video recordings will be accepted in lieu of in-person training.

Samples

(Note to A/E: add additional samples below as needed.)

The Roofing System Contractor shall submit representative samples of available The Manufacturer / Contractor Manufacturer color chart for selection by the A/E. Deliver sample(s) where directed.

Mockups:

(Note to A/E: Insert mockups below as required for aesthetics or constructability (required for all complex element transitions). Insert and edit the appropriate selection below.)

[None required.]

[In-situ mock-up is required for the following areas / elements: (A/E to list Section and Elements)]

[Free standing mock-up is required for the following areas / elements: (A/E to list Section and Elements)]

Installation Meetings

Prior to the start of construction, the GPC shall schedule an installation meeting. It is required that the GPC’s Project Manager and Superintendent; and Roofing System Superintendent and/or Foreman attend an installation meeting. Coordinate attendance with these representatives: DFD Project Representative, SME, the user Agency Representative, and the A/E. All required and accepted submittals for this Section and related work (including penetrations and curbs) shall be uploaded to DFD’s PMIS prior to the meeting.

(Note to A/E: add or remove paragraphs below as needed.)

[For projects with Lightning Protection Systems, the General Prime Contractor shall set up a meeting between the Roofing System Contractor, the Lightning Protection Contractor, and all other contractors as required to coordinate the attachment and final location of the Lightening Protection System.]

PART 2 - PRODUCTS

Performance Requirements

Roof Assembly shall have a U.L. Class A Fire Hazard Classification. Note: All exceptions shall be approved in writing by the DFD SME and DFD project manager.

Roof Assemblies shall be designed to, and have the assembly testing requisite and deliverable, to comply with the following standards, relative to the type, class, and geographic location of the work: American National Standards Institute / Factory Mutual – ANSI / FM 4474, American Society of Civil Engineers / Structural Engineering Institute – ANSI / SEI 7-16, American Society for Testing and Materials – ASTM E1592, Underwriters Laboratories – UL 580.

Manufacturers and Materials

All products installed on this Project shall be compatible with one another and approved by the Manufacturer for use in the Manufacturer / Contractor Manufacturer tested roof assembly / system and included in the Manufacturer / Contractor Manufacturer NDL warranty. All associated products required by the Manufacturer / Contractor Manufacturer for a complete warranty specified installation shall be approved and provided by the Manufacturer / Contractor Manufacturer. Unapproved Manufacturer products installed on the project shall be cause for rejection of the roof system in its entirety and shall be completely replaced at no cost to the project.

Use of salvaged materials shall be considered cause for rejection of the roof system in its entirety and shall be completely replaced at no cost to the Project, unless specified herein. Salvaged or used materials are unacceptable and shall be removed from the Project site.

All products installed on this project shall have been in production, and in field use (with field installed data upon request), for a minimum of ten (10) years. Products that do not meet the ten (10) year requirement that are installed on this project shall be rejected and replaced at no cost to the project.

DOUBLE LOCKING VERTICAL LEG SHEET METAL rOOF PANEL

(Note to A/E: select the system choices listed below from each category listed in red.)

Roll formed, Double Lock Vertical Leg Sheet Metal Roof panel, with a 1800 [1.5-inch (1½")] [2-inch (2")] high finished vertical leg, that has thermally applied in-seam sealant. Panels shall be factory-roll-formed or field-formed using equipment approved by the Manufacturer.

Double Lock Vertical Leg Sheet Metal Roof panel assembly shall have been tested to and passed the following criteria:

- Minimum Uplift Resistance – UL 580 Class 90

- Air Infiltration – ASTM E283, ASTM E1680

- Water Penetration – ASTM E331, E1646, ASTM E2140

- Fire Rating UL Class A Rated Assemblies, UL 263, UL 790

- Hail Impact Rating Class 4, UL 2218

Panel Material and Thickness – Base Metal:

[24 ga.] [22 ga.] [AISI G-90 Galvanized steel, minimum yield of 33 to 45 KSI]

[24 ga.] [22 ga.] [AZ-50 Hot Dipped Galvalume, minimum yield of 50 KSI]

Panel Width: [12"] [16"] [18"] [20"]

Stiffening Ribs: [None] [Pencil] [Flat] [Striations]

Panel Length: Continuous without transverse seams – no minimum / maximum.

Color: To be selected from Manufacturer's standard colors.

Texture: [Smooth] [Stucco Embossed]

Finish:

(Note to A/E: Fluoropolymer (FEVE) resin-based coatings are not the same as Kynar 500 / Hylar 5000 polyvinylidene fluoride (PVDF) resin coatings)

[Primed and coated on one side with a minimum 70% Kynar 500 / Hylar 5000 polyvinylidene fluoride (PVDF) resins premium fluoropolymer coating system of 1.0 (±0.1) mil total dry film thickness; With a wash coat of 0.3 – 0.4 mil dry film thickness applied to the reverse side, and strippable protective film.]

[Unfinished Galvalume]

FLASHING METAL

Trim flashing, valley flashing, ridge cap flashing, edge and rake flashing, counterflashing, and all other miscellaneous flashing metal, shall be provided by the same Manufacturer as the Double Locking Vertical Leg Sheet Metal Roofing System. Base metal material, thickness, finish, and color shall be same as the Double Locking Vertical Leg Sheet Metal Roofing System.

CLOSURE COMPONENTS

Zee Closure: 24-gauge steel with matching finish and color to the roof panels.]

Foam Closure / End Cap: Closed-cell, cross-linked polyethylene foam or EPDM rubber, die-cut or molded to the exact panel configuration, with a temperature range of -70°F to 200°F, a density of 1.5lb/ft³ to 2lb/ft³, and pre-applied adhesive strip.

ROOF PANEL ATTACHMENT CLIPS

(Note to A/E: The A/E is required to specify the clip type that is the most appropriate for the designed system, including specification of fixing points for panels with Expansion (Floating) clips. NOTE: For roof panels that are dark in color, wider than 18-inches (18"), or exceed 20-feet (20') in length, Expansion (Floating) clip systems that meet the specified wind uplift requirements are recommended.)

Roof Panel Attachment Clips shall be supplied by the Manufacturer and designed for use with the specified panel.

[Roof Panel Expansion (Floating) Clip: Two-piece design to allow for thermal movement of the panel. Manufactured from 300 series stainless steel with pre-punched holes for attachment to the substrate. Upper tab shall be mechanically integrated into the seam. Upper tab shall be of a solid or “butterfly” design as required by the Manufacturer for the warranted wind speed (uplift design pressures).]

[Roof Panel Fixed Clip: One-piece design manufactured from 300 series stainless steel with pre-punched holes for attachment to the substrate. Upper portion shall be mechanically integrated into the seam. Use only at the panel fixed point.]

Roof Panel Clip Fasteners: Low profile, epoxy applied electrocoated, panhead fasteners, in size #10 or #12, with Manufacturer design and specification for attachment of roof panel attachment clips to the substrate. Fasteners shall penetrate steel deck a minimum of 0.75-inches (¾") and a maximum of 1.5-inch (1½"). Fasteners shall penetrate through plywood decks or into wood board decks 1-inch (1").

[Roof Panel Bearing Plates: Manufacturer’s bearing plate designed for attachment of roof panel clips directly over insulation / cover boards, manufactured from 300 series stainless steel.]

Exposed Fasteners: Color matched screws, with metal backed weather tight washers. Steel washer shall be a minimum of 0.375-inch (⅜") diameter, with gaskets washers made of EPDM, neoprene, or other equally durable elastomeric material.

ICE & WATER PROTECTION MEMBRANE: High-temperature rated, granular-free polyethylene surface, self-adhering modified bitumen sheet, a minimum of 40-mil thickness, with an ASTM D-1970 compliant minimum service temperature rating of 2500 F, rated for use under metal roof panels, as a component in the Manufacturer approved assembly.

Synthetic Underlayment:

(Note to A/E: Specify synthetic underlayment for all roofs that require a slip-sheet material, or roofs that do not have a specified continuous Ice & Water Protection Membrane.)

Premium synthetic underlayment designed for use on roof decks as a water-resistant layer beneath Double Lock Vertical Leg Sheet Metal Roof panels. Underlayment shall be a component of a UL Listed ANSI/UL 790 Class A System when specified. Underlayment shall be rated for use under metal roof panels, as a component in the Manufacturer approved assembly. Underlayment shall bear labels indicating compliance.

CAP Nails: Corrosion resistant nails, with an 11-gauge (8-penny) or 12-gauge (7-penny) ringed shank, 0.375-inch (⅜") diameter head, and a fully affixed 1-inch (1") plastic cap. Nails to be of sufficient length to penetrate plywood deck or substrate, a minimum of 0.75-inch (¾"). Nails shall comply with ASTM F1667.

Thermal Barrier

[None Required]

[Pre-primed fiberglass faced gypsum board, ASTM C1177. Thickness as required by construction drawings.]

Insulation

(Note to A/E: When the roofing system will be directly applied to the unvented substrate, specify the insulation using this section. NOTE: When a ventilation system is required between the insulation boards and the roofing system, specify the insulation and plywood assembly within Section 07 22 16 – Ventilated Nail Base Insulation; the assembly shall be sub-specified as [Premanufactured Units] or [Field Fabricated Units].)

[None Required]

[Polyisocyanurate: flat stock, ASTM C1289 compliant, Type II, Class 1; rigid board insulation with coated glass mat facing on both sides. Thickness and slope as required by construction drawings. Individual board thickness shall not exceed 3-inches (3").

Insulation Fastener: Designed for use with fastening plates to secure insulation to metal or wood substrates. Fasteners shall have a drill point tip and buttress thread design to reduce back-out. Fasteners shall have a coating providing corrosion resistance exceeding the requirements of FM 4471. Thread diameter as required by the Manufacturer to obtain warranty.

Insulation Fastener Plates: Galvalume coated metal plates designed for use with fasteners listed above for attachment of insulation. Plates shall exceed the corrosion resistance requirements of FM 4471. Plate diameter shall be 3-inch (3") minimum for securing insulation.]

Spray foam insulation: Two-component, quick-cure polyurethane foam with a flame spread of less than FSI 25 and a density of 1.75 lb./ft.³. DOW FROTH-PAK Foam Insulation or accepted equal.

COVER BOARD

(Note to A/E: When the roofing system will be directly applied to the unvented substrate, specify the coverboard using this section. NOTE: When a ventilation system is required between the coverboard and the roofing system, specify the coverboard and plywood assembly within Section 07 22 16 – Ventilated Nail Base Insulation; the assembly shall be sub-specified as [Premanufactured Units] or [Field Fabricated Units].)

[None Required]

[High Density Polyisocyanurate: ASTM C1289 compliant, Type II, Class 4, Grade 1, 0.5-inch (½") thick, rigid flat stock insulation board, with coated glass mat facing on each side.]

[Fiberglass Faced Gypsum Board: ASTM C1177 compliant, high density gypsum core rigid flat stock board, <insert board thickness> thick, with fiberglass facings on each side.]

[Cover Board Fastener: Designed for use with fastening plates to secure cover board to metal or wood substrates. Fasteners shall have a drill point tip and buttress thread design to reduce back-out. Fasteners shall have a coating providing corrosion resistance exceeding the requirements of FM 4471. Thread diameter as required by the Manufacturer to obtain warranty.

Cover Board Fastener Plates: Galvalume coated metal plates designed for use with fasteners listed above for attachment of cover board. Plates shall exceed the corrosion resistance requirements of FM 4471. Plate diameter shall be 3-inch (3") minimum for securing insulation.]

RIDGE VENTILATION

(Note to A/E: Where specified, and in conjunction with a fully vented attic or nailbase assembly and soffit, the A/E shall calculate, verify, and specify, the appropriate balanced intake & exhaust ventilation adequate for the building.)

[Vented Ridge Cap Assembly:

24-gauge steel with matching finish and color to the roof panels, internal weather filter, external wind baffles, 15-square-inches (15 in.²) of net free area per 1-lineal-foot (1′) and tested to resist wind driven rain up to 110-miles-per-hour (110 mph), compliant to ASTM D3161 class F.]

[Vented Zee Closure assembly:

26-gauge steel with matching finish, and color to the roof panels, external wind baffles, 15-square-inches (15 in.²) of net free area per 1-lineal-foot (1′) and tested to resist wind driven rain up to 110-miles-per-hour (110 mph), compliant to ASTM D3161 class F.]

SNOW RETENTION SYSTEM

Snow retention system that is designed for non-penetrating attachment to Double Locking Vertical Leg Sheet Metal Roofing System. System shall have an aluminum rail that is able to accept a color matched insert, with rubber booted snow and ice clips that contact that reduce snow and ice slides under the rail.

Clamps: Manufactured from 6000 series aluminum extrusions conforming to ASTM B221, or aluminum castings conforming to ASTM B85, and to AA Aluminum Standards. Designed for non-penetrating attachment to vertical leg of standing seam panel.

Bolts and screws: 300 Series stainless steel manufacturer approved hardware.

Cross Member Rail: Manufactured from 6061-T6 alloy temper aluminum extrusions conforming to ASTM B221, and AA Aluminum Standards and Data, with a receptacle in face to receive color-matched metal strips. Note: Splice connectors are required for alignment and structural continuity at end joints.

Color Strips: Same material and finish as the roof panels.

Snow and Ice Clips: Aluminum, with rubber foot, that attaches to the cross-member rail between each standing seam.

ACCESSORY MOUNTING SYSTEM

(Note to A/E: Specify Type of support / attachment required. Use roller type supports when pipe / conduit expansion and contracting accommodations are needed.)

[None required.]

[System designed to mount solar, conduit, antennas, equipment, etc., with non-penetrating attachment to Double Locking Vertical Leg Sheet Metal Roofing System.

Clamps: Manufactured from 6000 series aluminum extrusions conforming to ASTM B221, or aluminum castings conforming to ASTM B85, and to AA Aluminum Standards. Designed for non-penetrating attachment to vertical leg of standing seam panel.

[Bolts and screws: 300 Series stainless steel manufacturer approved hardware.

Struts and Rails: Manufactured from 6000 series aluminum extrusions conforming to ASTM B221 and AA Aluminum Standards and Data.]

[Pipe Support: Adjustable height stainless steel or zinc plated support, with self-lubricating roller to allow for longitudinal pipe movement. Provide top pipe guide to restrain vertical movement of pipe. Support to attach to non-penetrating clamp.]

Miscellaneous

Plumbing Vent Flashing: Pre-molded [EPDM, to +250ºF, black or grey in color] [Silicone to +350ºF, red in color] boot, with moldable aluminum or stainless-steel base ring. Basis of Design: Buildex, Decktite, or equivalent, as acceptable by manufacturer.

Plumbing Vent Pipe Extension: Prefabricated plumbing pipe extension. Basis of Design: OMG Tubos Vent Pipe Extension, or equivalent, as acceptable by manufacturer.

[Pipe Stabilizer: Polycarbonate stabilizer arm designed to break apart snow slides and secure pipe upright and intact. Basis of Design: Vent Protect “Vent Protect”, or equivalent, as acceptable by manufacturer.]

Sealant: ASTM C920, Type S, Grade NS, Minimum Class 25, Use NT, M, A or O; FS TT-S-00230C, Type II, Class A; one-part polyurethane base, elastomeric joint sealing compound

Butyl Sealant Tape: 0.1875-inch (3/16") by 0.875-inch (⅞") double or triple bead butyl rubber tape designed for sealing metal roofs. As acceptable by manufacturer.

Butyl Sealant (Gun Grade): Non-skinning, non-sag gun grade butyl sealant designed for standing seam metal roofs. As acceptable by manufacturer.

[Expandable Sealant Tape: Self Adhering open-cell polyurethane foam impregnated with a water-based acrylic-modified asphalt emulsion. Designed to seal out moisture on metal roofs. Size to obtain a maximum of 80% compression form fully expanded size. Basis of Design: Emseal “AST Hi-Acrylic”, or equivalent, as acceptable to roof panel manufacturer.

[Foam Backer Rod: Closed cell non-absorbent polyethylene rod stock. ASTM D5249, size as required.]

Concrete Fasteners: Zinc alloy expansion shield with hardened steel pin or concrete screw.

Water Block Sealant (Mastic): Gun grade butyl base rubber designed to provide a seal when used in compression. Not for use as an exposed sealant.

Sealant: ASTM C920, Type S, Grade NS, Class 25, Use NT, M, G, A, or O; FS TT-S-00230C, Type II, Class A; 1-part polyurethane base, elastomeric joint sealing compound such as Sika Chemicals "Sikaflex 1a", Sonneborn-Contech "Sonolastic NP1" or Tremco "Vulkem 116" or “Dymonic".

Metal to Metal: #10 by 0.75-inch (¾”) self-drilling, self-tapping, stainless steel sheet metal screws with pan or hex heads. Screw to have an integral metal-backed EPDM or neoprene washer.

Note: Other products, not specifically described, but required for a complete and proper warranted system installation as required by this section shall be selected by the Contractor to be included in the Work, identified on a materials list and subject to the approval of the Owner.

PART 3 – EXECUTION

Examination

Prior to commencement of work, the Roofing System Contractor shall examine the areas and conditions under which work in this section shall be installed. Notify the DFD’s Project Representative, GPC and A/E of any conditions detrimental to the proper and timely completion of the work (safety or otherwise). The Roofing System Contractor shall not proceed until the unsatisfactory conditions have been corrected.

The Roofing System Contractor shall inspect the underside of the structural deck for spray-applied insulation or fireproofing, as well as interior components attached to the deck. Notify DFD’s Project Representative, GPC and A/E of such items that could be damaged or dislodged from deck during normal construction activities. The Roofing System Contractor shall take every precaution to prevent damage to, or, the release of components from the interior building envelope during construction. The GPC is responsible for all damage to the building interior or its contents that occur as a direct cause of the work, and due to the means and methods utilized to accomplish the work required herein.

Note: Proceeding with the work shall signify the Roofing System Contractor’s acceptance of the condition of the substrate that is to be covered by this work.

Site Conditions

Apply roofing materials in dry weather. All roofing materials installed during a rain / snow/ precipitation event, shall be removed and replaced with dry materials at the Roofing System Contractor's expense.

Note: Do not apply roofing during ambient air temperatures below 32-degrees (32°) Fahrenheit, without prior written approval from the DFD SME. Alternate System Options for applying roofing during ambient air temperatures below 32-degrees (32°), are aviaible with written approval from DFD. Any adhered roofing material applied below 32-degrees (32°) Fahrenheit without prior written approval shall be rejected.

The GPC shall provide special protection or avoid any heavy traffic on work to remain.

Existing materials designated to remain, which are damaged or defaced prior to the installation of new work, shall be replaced at the GPC’s expense to like new condition. Do not store equipment or materials on completed work.

Extend plumbing vent stacks as necessary to provide a minimum height of 8-inches (8") above the finished roof surface. Adjust existing stack height as required so that the joint between the extension and the existing pipe occurs below the roof flashing.

Note: If existing pipe penetrations occur within 2-inches (2") from a vertical leg, consult the A/E to verify constructability of pipe relocation – pipe flashing bases require a 2-inches (2") minimum clearance.

Install all rooftop mounted equipment in a Manufacturer approved, watertight manner, and repair any damage to sheet metal or other components related to connection and protection of the roof system.

Prevent materials and debris from entering or clogging the gutters, downspouts, roof drains, and conductors. Remove plugs when no work is taking place, at the end of the day, or when rain is forecast.

Substrate Preparation

(Note to A/E: Use appropriate Sections from Division 7 to specify removal and disposal of existing roofing system and related components.)

Clean surfaces of all residual materials as necessary to ensure adequate bond of new material.

The Roofing System Contractor shall verify that the substrate is clean, dry, free from sharp projections and depressions, and that all surfaces and site conditions are ready to receive new materials. All areas (including bottom flanges / ribs of steel deck) shall be devoid of any moisture and all other debris prior to the start of Roofing System construction.

The Roofing System Contractor shall take whatever action is necessary to prevent dirt, debris, and toxic fumes from entering the building during the work required by this Section.

The Roofing System Contractor shall verify that wood blocking, curbs, and nailing flanges are securely anchored, and that roof openings and penetrations are in place, set, and braced.

The Roofing System Contractor shall notify the DFD Construction Representative, GPC and the A/E if the existing deck has uncovered holes, is found to be improperly fastened, deteriorated, decayed, or deformed, or in any way preventing proper installation or drainage of the new system.

installation of thermal barrier

(Note to A/E: IBC code requires the design professional (A/E) to calculate proper wind design for all roofing projects. Calculate and insert all zoned mechanical attachment quantity and spacing requirements for the thermal barrier, using the ASCE 7/16 standards, including any additional requirements to obtain the specified manufacturer wind warranty. Insert the attachment calculations below. Add or remove paragraphs below based on roof deck type and insulation attachment.

If the common mechanical attachment method is utilized (mechanical attachment of thermal barrier and insulation substrate layer using common fasteners), attachment requirements for the cover board shall only be required in the insulation section – A/E to create custom note in this section to reference the common attachment method and attachment rates in the insulation section).

[None required.]

[Clean deck surfaces prior to application. All deck surfaces, including bottom flanges / ribs of steel deck, shall be devoid of any moisture and all other debris prior to the start of thermal barrier installation.

The thermal barrier shall be mechanically attached to the deck with fasteners and plates.

For metal decks, fasteners shall be of a length to engage the top plane (rib) of the deck and not extend beyond the bottom plane of the deck.

Loose lay thermal barrier across deck. Lay with long joints in a continuous condition that is parallel to deck ribs and short joints staggered. Joints parallel to deck ribs shall be formed over with edges bearing a minimum of 1.5-inches (1½″) on deck flange.

The Roofing System Contractor shall attach the thermal barrier using the attachment rates listed below:

Field (Zone 1): shall consist of the interior field dimensions throughout the roof plane. Field shall be mechanically attached a rate of <insert number> fasteners and plates per square foot (<insert number>/ft.²).

Perimeter (Zone 2): shall consist of an area <insert perimeter width> feet wide from the exterior roof edge inward to the interior field, continuously around the perimeter, excluding corner zones. Perimeter shall be mechanically attached a rate of <insert number> fasteners and plates per square foot (<insert number>/ft.²).

Corner (Zone 3): shall consist of an area <insert corner dimension in (<number> feet by <number> feet)> wide from all roof corner conditions. Corners shall be mechanically attached at a rate of <insert number> fasteners and plates per square foot (<insert number>/ft.²).]

Installation of Insulation System

(Note to A/E: IBC code requires the design professional (A/E) to calculate proper wind design for all roofing projects. Calculate and insert all zoned mechanical attachment quantity and spacing requirements for all layers of the insulation system (excluding the cover board), using the ASCE 7/16 standards, including any additional requirements to obtain the specified manufacturer wind warranty. Insert the attachment calculations below. Add or remove paragraphs below based on roof deck type and insulation attachment.)

[None required.]

Repair all damage to vapor retarder before installation of first layer of insulation.

Clean all deck surfaces prior to application of insulation. All deck surfaces, including bottom flanges / ribs of steel deck, shall be devoid of any moisture and all other debris prior to the start of installation.

Stagger insulation joints in all layers of insulation, a minimum of 12-inches (12") in both directions. Insulation shall be installed in a minimum of two (2) layers.

Provide tapered insulation saddles at twice the slope of field taper, on the backside of curbs and rails.

Install insulation boards with edges in moderate contact without forcing. Cut insulation to fit neatly to perimeters of roof areas and around penetrations and projections.

Fill gaps between 0.25-inch (¼") and 0.5-inch (½") wide with spray foam insulation. Gaps over 0.5-inch (½") shall be filled with specified insulation board material.

The Roofing System Contractor shall attach the system insulation using the attachment rates listed below:

Field (Zone 1): shall consist of the interior field dimensions throughout the roof plane. Field shall be mechanically attached a rate of <insert number> fasteners and plates per square foot (<insert number >/ft.²).

Perimeter (Zone 2): shall consist of an area <insert perimeter width> feet wide from the exterior roof edge inward to the interior field, continuously around the perimeter, excluding corner zones. Perimeter shall be mechanically attached a rate of <insert number> fasteners and plates per square foot (<insert number >/ft.²).

Corner (Zone 3): shall consist of an area <insert corner dimension in (<number> feet by <number> feet)> wide from all roof corner conditions. Corners shall be mechanically attached at a rate of <insert number> fasteners and plates per square foot (<insert number >/ft.²).

Install fasteners perpendicular to roof deck using a standard clutch drive screw gun. Screw threads shall engage metal deck minimum of 0.75-inches (¾"), maximum of 1.5-inches (1½").

Do not under drive fasteners or over drive fasteners breaking the insulation facer. Replace insulation boards with damaged facer material.

For metal decks, fasteners shall be of a length to engage the top plane (rib) of the deck and not extend beyond the bottom plane of the deck.]

INSTALLATION OF COVER BOARD

(Note to A/E: IBC code requires the design professional (A/E) to calculate proper wind design for all roofing projects. Calculate and insert all zoned mechanical attachment quantity and spacing requirements for the cover board), using the ASCE 7/16 standards, including any additional requirements to obtain the specified manufacturer wind warranty. Insert the attachment calculations below. Add or remove paragraphs below based on roof deck type and insulation attachment.)

[None required.]

Repair all damage to vapor retarder before installation of coverboard.

Clean all deck surfaces prior to application of coverboard. All substrate surfaces, including bottom flanges / ribs of steel deck, shall be devoid of any moisture and all other debris prior to the start of installation.

Stagger all coverboard joints a minimum of 12-inches (12") in all directions.

Provide tapered insulation saddles beneath coverboard, at twice the slope of field taper, on the backside of curbs and rails.

Install coverboards with edges in moderate contact without forcing. Cut insulation to fit neatly to perimeters of roof areas and around penetrations and projections.

Fill gaps between 0.25-inch (¼") and 0.5-inch (½") wide with spray foam insulation. Gaps over 0.5-inch (½") shall be filled with specified insulation board material.

The Roofing System Contractor shall attach the coverboard using the attachment rates listed below:

Field (Zone 1): shall consist of the interior field dimensions throughout the roof plane. Field shall be mechanically attached a rate of <insert number> fasteners and plates per square foot (<insert number >/ft.²).

Perimeter (Zone 2): shall consist of an area <insert perimeter width> feet wide from the exterior roof edge inward to the interior field, continuously around the perimeter, excluding corner zones. Perimeter shall be mechanically attached a rate of <insert number> fasteners and plates per square foot (<insert number >/ft.²).

Corner (Zone 3): shall consist of an area <insert corner dimension in (<number> feet by <number> feet)> wide from all roof corner conditions. Corners shall be mechanically attached at a rate of <insert number> fasteners and plates per square foot (<insert number >/ft.²).

Install fasteners perpendicular to roof deck using a standard clutch drive screw gun. Screw threads shall engage metal deck minimum of 0.75-inches (¾"), maximum of 1.5-inches (1½").

Do not under drive fasteners or over drive fasteners breaking the insulation facer. Replace coverboards with damaged facer.

For metal decks, fasteners shall be of a length to engage the top plane (rib) of the deck and not extend beyond the bottom plane of the deck.]

Installation of ice & water protection membrane

(Note to A/E: Add or remove paragraphs below based on substrate and underlayment requirements.)

Clean and prepare the roof deck to receive the new roof system. Roof deck shall be clear of all debris, and abrasive protrusions such as underdriven nails. Surfaces shall be dry and free of dust and foreign material prior to application. Note: Ice & water protection membrane shall only be installed over continuous deck conditions.

Install ice & water protection membrane per specifications listed herein, and in compliance with the manufacturer's additional detailed instructions, directly to the [deck] [insulation] substrate as follows:

Install ice & water protection [continuously across the roof deck] [with 2-courses minimum along all eaves] as specified. Lay ice & water protection membrane smooth without wrinkles. Note: Ice & water protection shall extend a minimum of 18-inches (18") past the plane of the exterior wall to roof intersection of the buildings’ conditioned space.

[Prime substrate with manufacturer’s primer if required by manufacturer.]

Install a full width sheet of ice & water protection membrane along the entire length of all rake edges. Extend down and overlap onto ice & water protection membrane at eave. Extend down fascia a minimum distance of 2-inches (2"), but no further than what will be covered by fascia metal, drip edge, or gutter.

Install ice & water protection membrane under all complex eave and rake transition planes.

At vertical facet abutments, extend ice & water protection membrane up the facet 6-inches (6").

Overlap ice & water protection membrane, using horizontal laps a minimum of 3-inches (3"), and vertical joints (end laps) end laps a minimum of 6-inches (6"). Offset all vertical joints. Lap material in direction of flow of water.

At intersecting wall lines install an 18-inch-wide (18") sheet of ice & water protection membrane, minimum, the entire length of wall, that shall extend up the wall 6-inches (6"). Prime wall if necessary to achieve bond to wall. Seal top of ice & water backup protection membrane to wall.

Ice & water protection membrane shall be installed at all perimeters, curbs, and penetrations (including pipes). Ice & water protection membrane shall be turned up a minimum of 2-inches (2"). Note: All temporary conditions shall be sealed with sealant specified herein.

After installation of the eave metal, provide a minimum 4-inch-wide (4") strip of ice & water protection membrane or flashing tape adhered to underlying ice & protection membrane and eave metal deck flange.

[Install a full width sheet of ice & water protection membrane centered down entire length of valley. Ensure the membrane is tightly pressed into valley line and extends across the eave and rake edges onto the fascia a minimum distance of 2-inches (2"). Valley membrane edges shall be overlapped by the field sheet a minimum of 6-inches (6").

After installation of valley metal, seal edges of metal with minimum 4-inch (4") width strip of ice & water protection membrane or flashing tape.]

All penetrations and vertical wall transitions that do not have a mechanical lap existing, shall be sealed with a caulk bead, sealant, or mastic to prevent water entry.

Ice & water protection membrane shall be secured using specified cap nails.

INSTALLATION OF SYNTHETIC UNDERLAYMENT

Clean the entire roof surface to remove loose nails, staples, granules, wood dust/particles and other debris prior to installation of underlayment.

Install one layer of synthetic underlayment parallel with eave over the entire roof deck area, parallel to the eaves, including the overlayment of areas with self-adhering ice & water protection membrane already installed. Overlap horizontal laps (side laps) a minimum of 2-inches (2"), overlap vertical joints (end laps) a minimum of 6-inches (6"). Offset all vertical joints.

Install synthetic underlayment over edge metal along eaves.

Install synthetic underlayment under edge metal along rakes.

Install synthetic underlayment a minimum overlap of 6-inches (6") from each side on all hips and ridges.

At intersecting wall lines extend synthetic underlayment up the wall 6-inches (6"). Seal top of synthetic underlayment to ice & water backup protection membrane and wall.

Seal synthetic underlayment watertight to penetrations.

At valleys, cover ice & water protection membrane with synthetic underlayment.

Lay smooth without wrinkles. Secure underlayment sufficiently until shingles are installed. Do not use synthetic underlayment as a temporary roof. Provide shingle roof covering at the end of each day.

Synthetic underlayment shall be secured using specified cap nails. Space fasteners a maximum of 6-inches-on-center (6"o.c.) on both head and end laps, and 12-inches-on-center (12"o.c.) in the field area in the center of the roll. Provide additional attachment as necessary until metal panels are installed.

Installation of DOUBLE LOCKING VERTICAL LEG SHEET METAL rOOF PANELs

(Note to A/E: IBC code requires the design professional (A/E) to calculate proper wind design for all roofing projects. Using the ASCE 7/16 standards, the A/E is required to calculate the uplift pressures and zones required for the system, including any warranty requirements, and insert them below. The A/E is also required to key and depict the uplift pressures and zones for the Double Locking Vertical Leg Sheet Metal System on the plan sheets. The A/E is NOT required to specify the clip type, gauge, spacing or fastening; The A/E shall validate the uplift design through the Assembly Letter and Shop Submittal processes. Add or remove paragraphs below as needed.)

Install continuous length Double Locking Vertical Leg Sheet Metal Roof Panel system in accordance with the Manufacturer’s instructions and engineering, installation drawings, Construction Documents, and accepted shop drawings, to provide for a weathertight installation that allows for thermal movement.

Clean and prepare the roof deck to receive the new roof system. Roof deck shall be clear of all debris, contaminates, and abrasive protrusions (such as underdriven nails). Surfaces shall be dry and free of dust and foreign material prior to application.

Roof panels shall have a layout and installation that is perpendicular to eave, symmetrical to adjacent roof areas, and avoids the placement of panel legs within 2-inches (2") of wall of plumbing vent pipes. Note: plumbing vent pipes shall be relocated if the 2-inch (2") minimum clearance to the wall of plumbing vent pipes is unachievable by layout modification.

Roof panels shall be cut with sharp clean shears (hand or machine). Note: Use of saws or grinding wheels to cut roof panels shall be cause for rejection of work.

Roof panel attachment clips shall be installed using the specified A/E approved engineering method, fasteners, and spacing. At time of installation, expansion and contraction design allowances shall be confirmed with the A/E.

The Manufacturer / Manufacturer Contractor shall provide Roofing System Contractor shall install a system that is rated and warrantied for the following pressure in the zones listed below:

Field (Zone 1): shall be designed for a system uplift pressure of < insert number > lb./ft², throughout the interior field of the roof plane (all areas excluding Zone 2 and Zone 3).

[Zone 1 attachment shall be installed using [expansion clips] [fixed clips] attached along the roof panel edge, at increments of < insert clip spacing in inches > starting at < insert distance in inches> from the roof plane edge and terminating < insert distance in inches> from the opposing roof plane edge / ridge.]

Perimeter (Zone 2): shall be designed for a system uplift pressure of < insert number > lb./ft², in the area <insert perimeter width> feet wide from the exterior roof edge inward to the interior field, continuously around the perimeter, excluding Zone 3.

[Zone 2 attachment shall be installed using [expansion clips] [fixed clips] attached along the roof panel edge, at increments of < insert clip spacing in inches > starting at < insert distance in inches> from the roof plane edge.]

Corner (Zone 3): shall be designed for a system uplift pressure of < insert number > lb./ft², in the area <insert corner dimension in (<number> feet by <number> feet)> wide from all roof corner conditions.

[Zone 3 attachment shall be installed using [expansion clips] [fixed clips] attached along the roof panel edge, at increments of < insert clip spacing in inches > starting at < insert distance in inches> from the corners of the roof plane.]

[The roof panel system shall be installed as detailed with an < insert the allowance for expansion and contraction in X-inch (X") > allowance expansion and contraction in the appropriate elements.]

[Provide roof panel expansion clips appropriately set to allow for expansion and contraction of the roof panel. Positioning of the sliding portion of the expansion clip is dependent on temperature at time of installation. Prior to installation, consult with A/E for proper positioning of the sliding portion of the expansion clip and verify fixing points.]

[Straight roof panel runs shall have a fixing point for the anchor clips at < insert location of fixed point >.]

[Radiused roof panels runs shall have a fixing point for the anchor clips at apex of curvature with expansion / contraction towards eave and headwall.]

[Secure each roof panel anchor clip with a minimum of two (2) fasteners into the underlaying deck.]

[Secure each roof panel anchor clip with a minimum of two (2) fasteners through a bearing plate into the underlaying structural deck.]

[Install < insert diameter of the foam rod > diameter foam rod stock below the center of each individual roof panel to mitigate panel deformation from thermal expansion.]

After the installation of the first roof panel on a facet, successive roof panels shall be installed without deformation that affects the modularity of the panel (distortion across the panel width dimension).

Fold tab ends of roof panel seams over the end of the seam to close off the end of the seam. Provide concealed sealant inside the end of the seam, prior to folding over tab. Fold the tab to the inside of the seam prior to seaming panel, locking tab into seam to prevent tab from pulling away with sliding snow / ice.

Roof panels shall be fabricated to have 1-inch (1") bottom locking open hemmed edge, that seats over the eave edge flashing, and seat/nest tightly over the eave edge flashing. Roof panels shall be taper cut at the edges as needed. Provide 3 beads of butyl sealant between pieces. Position the roof panel over the installed eave edge flashing, accommodating for expansion and contraction, and then crimp the roof panel to the eave edge flashing across the entire panel length.

[Roof panels shall be fabricated to have 1-inch (1") bottom locking open hemmed edge, that seats over the 1-inch (1") integral topside open locking hem of the valley flashing, and is broken parallel to valley plane. Roof panels shall be taper cut at the edges as needed. Provide 2 beads of butyl sealant between pieces. Position the roof panel over the installed valley flashing, accommodating for expansion and contraction.]

Roof panels shall be mechanically seamed to a complete 1800 double lock of the leg, (900 primary, 900 secondary), with the finish locks parallel to the starting degree of the vertical leg. Roof panel anchor clips shall be integrally locked into the leg. Take extreme care during seaming of panels so that seamer does not run off seam causing seam or panel deformation. Note: Deformation of seam or panel shall be cause for rejection of the work.

Note: Roof panels shall, at a minimum, have the primary lock field hemmed across the full length of the vertical leg of the panel at the end of every workday.

Provide prefabricated boot flashings at round penetrations. Secure boot flange to roof panel over a bed of

sealant, using the Manufacturer’s specifications for fastening.

Roof panels shall be turned up at terminations a minimum of 2-inches (2"), as closure and flashing heights allow, and as detailed. Closures, flashing, and counterflashing shall be installed as per related Sections.

Apply supplemental sealants as specified, detailed, and required by the Manufacturer.

INSTALLATION OF FLASHING WITH PANEL TERMINATION

All shop broken or field broken flashing and edging pieces, shall be fabricated and installed as specified, as depicted, as per the Manufacturer’s warranty requirements and herein.

Pieces shall be formed true to shape, accurate in size, square, and free from distortion or defects. Do not “punch” metal at brake points.

Flashings at all conditions or abutments (walls, curbs, etc.), parallel with the roof panel run, shall have matching allowances expansion and contraction as roof panel.

Pieces shall be formed in lengths of 8-feet (8'-0") or 10-feet (10'-0") where practical. All pieces shall be a minimum of 3-feet (3') in length, unless comprised of the entire run.

Unless detailed otherwise, hem all exposed edges on underside. Vertical facet flashing shall have a surface tension break / “drip”, that consists of a hemmed bottom edge.

All non-locking flashing pieces shall have a minimum overlap of 3-inches (3"); Refer to the drawing sets and the Manufacturer’s warranty requirements for specific conditions.

When lapping flashing pieces, taper cut and remove portions of the hem to allow the cap pieces to seat/nest tightly.

Outside corners shall be fabricated such that the outside face of the section is broken at corner. Miter and seam top of outside and inside corners using rivets and specified sealant. Corner pieces shall be a minimum of 18-inches (18") in length, in both directions from the corner. Note: Seams at corner conditions shall be cause for rejection.

All flashing shall be lapped with the base piece installed first and closest to the drainage point, and each successive piece overlaying on the top side of the previous piece. Note: All sieve laps shall be rejected regardless of sight lines.

Roof Edge Flashing:

(Note to A/E: Detail extended eave / rake edge metal and panel hem to accommodate panel design expansion and contraction. If a metal fascia assembly is required, specify the fascia assembly in Section 07 63 00 Sheet Metal Specialties.)

Fabricate the eave / rake edge flashing with a flange that extends a minimum of 3-inches (3") onto the roof deck and a minimum of 1-inch (1") past the vertical plane of the fascia (for securement of the roof panel, 4-inches (4") total minimum), and a leg that extends a minimum of 3-inches (3") onto the fascia, or as required to conceal the ice & water shield. Note: Vertical legs along fascia conditions shall be utilized for end run locks, if compliant with Manufacturer system warranty specification and specified herein. Joggle or bullnose cleats shall not be allowed without prior approval from the A/E and DFD project representative.

Eave edge flashing shall be installed prior to synthetic underlayment (underneath), and rake edge flashing shall be installed after the synthetic underlayment (over-top).

Roof edge flashing shall be installed with laps in direction of water flow, and along eave edges with the exposure facing away from the entrances or high visibility areas if constructable.

Taper cut and remove portions of the extended leg hem and drip hem to allow pieces to seat/nest tightly. Provide thin amount of butyl sealant between pieces.

Roof edge flashing shall be secured by installing the specified fasteners through the deck flange 3-inches-on-center (3"o.c.), staggered by 0.5-inches (½"), and approximately 1-inch (1") in from edge of flange.

Where the roof edge flashing abuts the wall, turn the deck side facet of the flashing up the wall a minimum of 2-inches (2"). The facet shall be overlayed with closures and finished with flashing.

Position the roof panel over the installed eave edge flashing, accommodating for expansion and contraction, and then crimp the roof panel to the eave edge flashing across the entire panel length.

Panel Termination at Sidewall:

Panel shall be terminated at the sidewall (perpendicular with the eave), by fitting the panel to or around the sidewall using relief cuts, to the leave the remaining flange (the panel pan). The remaining relief cut flange will be field bent up to a degree matching the sidewall and have a 0.75-inch (¾") topkick, broken at 450 to allow for a caulk bead. The relief cut flange shall be notched with elongated holes, 12-inches-on-center (12"o.c.), and fastened at the same rate, considering expansion and contraction allowances. The flashing flange and fastener heads shall be sealed with the specified sealant and finished with a counter flashing.

All roof panel termination at eave, rake, curb, wall, hip, ridge, or any other condition that has a locking or fixing point, shall have an allowance for panel expansion and contraction.

Panel Termination at Headwall / High Side:

Panel shall be terminated at the headwall / high side (parallel with the eave), by fitting the panel to or around the headwall / high side using relief cuts, to the leave the remaining flange (the panel pan). The remaining relief cut flange will be field bent up to a degree matching the headwall / high side and have a 0.75-inch (¾") topkick, broken at 450 to allow for a caulk bead. The relief cut flange shall be fastened at rate of 12-inches-on-center (12"o.c.). The flashing flange and fastener heads shall be sealed with the specified sealant, watertight to panel legs, and finished with a counter flashing.

All roof panel termination at eave, rake, curb, wall, hip, ridge, or any other condition that has a locking or fixing point, shall have an allowance for panel expansion and contraction.

Zee Closure:

Install zee closures as specified for panel terminations, flashing, and Manufacturer warranty requirements. Note: Zee closures are required for all plane transition flashing unless otherwise specified.

Zee closures shall be set between panel legs along facets parallel to the eave (horizontal runs), and continuously along facets perpendicular to the eave (vertical runs). Notch the zee closures to fit tightly between the vertical legs, leaving no gaps for snow/water intrusion on horizontal runs, and lapped a minimum of 2-inches (2") with lap facing down slope and nested tightly on vertical runs. Fasten the zee closure 4-inches-on-center (4"o.c.), through double beaded butyl tape to metal panel only, do not fasten to substrate unless termination is a fixed point.

All zee closure base flashing assemblies require finish with a 24-gauge steel that is a matching finish and color to the roof panels and has 1-inch (1") open hemmed edges on the horizontal flange, that seat over the zee closure.

All interior gaps, lap joints, end laps, penetrations, and exposed fasteners shall be sealed on the concealed side. Seal the zee closure and fastener heads by back caulking / caulking, as specified.

Sidewall Flashing:

Contractor to notify the DFD Project Representative and A/E prior to the beginning of work, if the detailed flashing or subsequent counter flashing will overlap / occlude the through-wall flashings or weep holes.

Sidewall flashing shall be fabricated of 24-gauge steel with matching finish and color to the roof panels.

[Sidewall flashing shall be installed in tandem with zee closure and have 1-inch (1") open hemmed edges on the horizontal, that seat over the zee closure. Taper cut and remove portions of the sidewall flashing hem and corner tabs to allow the pieces to seat/nest tightly into the zee closure, and against the vertical facet. Provide 3 beads of butyl sealant between pieces. Overlap the counter flashing pieces 3-inches (3"). Crimp the sidewall flashing to the zee closure across the entire run length. Fasten sidewall flashings using screws with weather-tight washers, as specified. Seal all joints and fastener heads with the specified sealant.]

[Sidewall flashing shall be installed over all vertical base flashing elements that require a transitional flashing to overlap the base flashing / relief cut flange and underlap the siding or trim elements. Sidewall flashing shall extend to within 1-inch (1") of the plane of the finished roof, or the closure assembly flashing, and shall be broken with a (spring action) longitudinal crease.]

The sidewall flashing shall extend vertically upward to underlap the siding or trim elements a minimum of 3-inches (3") or terminate into a reglet for masonry conditions. All corner tabs shall extend to a minimum of 3-inches (3") past the plane of the corner.

Headwall / High Side Flashing:

Contractor to notify the DFD Project Representative and A/E prior to the beginning of work, if the detailed flashing or subsequent counter flashing will overlap / occlude the through-wall flashings or weep holes.

Headwall / high side flashing shall be installed in tandem with zee closure, shall be fabricated of 24-gauge steel with matching finish and color to the roof panels, and have 1-inch (1") open hemmed edges on the horizontal, that seat over the zee closure. The headwall / high side flashing shall extend vertically upward to underlap the siding or trim elements a minimum of 3-inches (3") or terminate into a reglet for masonry conditions. All corner tabs shall extend to a minimum of 3-inches (3") past the plane of the corner.

Taper cut and remove portions of the headwall / high side flashing hem and corner tabs to allow the pieces to seat/nest tightly into the zee closure, and against the vertical facet. Provide 3 beads of butyl sealant between pieces. Overlap the headwall / high side flashing pieces 3-inches (3"). Crimp the headwall / high side flashing to the zee closure across the entire run length. Fasten sidewall flashings using screws with weather-tight washers, as specified. Seal all joints and fastener heads with the specified sealant.

Hip / Ridge Cap Flashing:

Ridge cap shall be fabricated to have open hemmed edges that seat over the zee closure. Taper cut and remove portions of the hem to allow the cap pieces to seat/nest tightly. Provide a bead of butyl sealant between the top of zee closure and underside of the ridge cap. Position the ridge cap over the installed zee closure, and in contact with the vertical leg. Overlap the ridge cap pieces 3-inches (3"), with 3 beads of butyl sealant between pieces. [For hip cap, install with lap facing down slope.] Provide sealed metal end cap(s) at termination(s). Crimp the ridge cap to zee closure across entire run length. All interior gaps, lap joints, end laps, penetrations, and exposed fasteners shall be back caulked / caulked.

Valley Flashing:

Valley flashing pieces shall be fabricated with a minimum extension of 12-inches (12") outward on each side of the valley, from the centerline. Valley flashing pieces shall be fabricated with a 1-inch by 1-inch (1"x1") high (minimum) inverted “V” profile, down the centerline of the flashing (“W” profile), and 1-inch (1") integral topside open locking hems back hemmed 0.5-inches (½"), across the side lengths for cleating on the outer edge.

Valley flashing pieces installed at the eave shall have a 1-inch (1") bottom side open locking hem that is broken parallel to the eave plane. Valley flashing shall be locked onto the roof edge flashing and crimped across the entire piece. The inverted “V” shall be balk caulked and tabbed to make watertight.

Secure each side of the valley flashing with 2-inch (2") wide cleats, made of matching material, 24-inches-on-center (24"o.c.) maximum. Lock free end of cleat into the 0.5-inch (½") open hem along each side of the valley flashing. Fasten the cleat to deck with 2 screws as specified.

Overlap successive valley flashing pieces 8-inches (8"), with 3 beads of butyl sealant concealed between pieces, and overlapped toward drainage. Taper cut and remove portions of the integral locking hem to allow valley flashing pieces to seat/nest tightly. Note: At intersecting valley runs, neatly seal, trim, and nest the intersecting valley flashing pieces maintaining the minimum standards herein.

After installation of valley metal, seal both sides of valley metal and cleats with 6-inch-wide (6") strip of ice & water protection membrane or flashing tape (minimum), across the integral topside locking hem, taking care to not overlap into the open hem.

Roof Flashing at Curbs:

(Note to A/E: Curbs shall be specified to be 8-inches higher than top of cricket.)

Curbs shall be securely mounted to the structural deck. Note: Saddles / crickets are required on up-slope side of all curbs to direct water around curb.

Flashing at curbs shall extend up the length of the vertical abutment (condition) and terminate with a flange that extends a minimum of 1-inch (1") across the top of curb’s horizontal top facet.

Saddle / Cricket Flashing:

(Note to A/E: Provide details of the saddle / cricket flashing and structural support.)

All upslope vertical facet abutments that are horizontally (perpendicular to the eave) wider than 12-inches (12") across, lack bi-directional drainage, or have a pitch of less than 3-inches in 12-inches (3":12"), shall have a saddle or cricket flashing installed.

Saddles / crickets shall be installed over solid decking. Fabricate cricket with watertight sealed seams. Crickets shall extend past the side walls of the penetration a minimum of 4-inches (4") on each side.

Saddle / cricket flashings shall be of a minimum offsetting pitch to return drainage to the roof field; 3-inches in 12-inches (3":12") or greater.

Saddle / cricket flashings shall have a flange that extends a minimum of 12-inches (12") onto the roof deck plane, with a 1-inch (1") integral topside open locking hems back hemmed 0.5-inches (½"), across the side lengths for cleating on the outer edge, and a vertical flange that extends a minimum of 12-inches (12") upward along all sidewalls and vertical facet abutments. The vertical flange seat within or be compatible to the closure flashing assembly or any siding, trim, or counter flashing assemblies.

Saddle / cricket flashing shall have all field seams soldered prior to installation.

Pipe Flashing:

Pipe penetration shall be secured under the structural deck preventing vertical and horizontal movement.

Flash round penetrations, such as soil vent stacks in accordance with manufacturers' instructions using prefabricated boots.

Install the prefabricated boot centered over pipe, securing the base of boot to roof panel over a bead of butyl sealant, using the specified fasteners. The base of the prefabricated boot shall be a minimum of 2-inches (2") from any vertical leg or abutment, move the penetration as needed. Seal top of exposed fasteners with cone shaped sealant.

Expansion Joint Flashing:

(Note to A/E: Provide expansion joints at location of building expansion joints. If required, show location of expansion joint(s) on plan. Provide plan notation and detail sets for expansion joints, with measurements indicating anticipated joint movement. For specific systems, or if existing expansion joints are inadequate, specify the location of required additional expansion joints. Select and detail expansion joint type below.)

Provide raised expansion joints, as shown on plans and detailed, the full length of roof panel at all building expansion joints. Refer to detail sets and Manufacturer’s recommendations for additional expansion joints.

[Flashing at expansion joints shall extend up the length of the vertical abutment (condition) and have a double hemmed “T” return flange that terminates by a minimum of 1-inches (1") across the top of horizontal surface, and a minimum of 1-inch (1") outward past the vertical plane of the fascia.]

[Terminate field panels at expansion joint as detailed. Install zee closures on each side of the expansion joint, using 3 beads of butyl sealant between the bottom of the zee closure and the roof panel. Install zee closures parallel to the expansion joint using specified fasteners.]

Expansion joint cap flashing shall be fabricated to have open hemmed edges that seat over the [T flange] [zee closure]. Taper cut and remove portions of the cap flashing hem to allow the pieces to seat/nest tightly. Provide 3 beads of butyl sealant between pieces. Overlap the cap flashing pieces 3-inches (3"). Install with lap facing down slope. Provide sealed metal end cap(s) at termination(s). Crimp the cap flashing to the [T flange] [zee closure] across the entire run length. Fasten cap flashings using screws with weathertight washers as specified.

All interior gaps, lap joints, end laps, penetrations, and exposed fasteners shall be back caulked / caulked.

Counter Flashing:

Contractor to notify the DFD Project Representative and A/E prior to the beginning of work, if the detailed flashing or subsequent counter flashing will overlap / occlude the through-wall flashings or weep holes.

Counter flashing to be used in tandem with zee closure, shall be fabricated of 24-gauge steel with matching finish and color to the roof panels, and have 1-inch (1") open hemmed edges on the horizontal, that seat over the zee closure. The counter flashing shall extend vertically upward to underlap the siding or trim elements a minimum of 3-inches (3") or terminate into a reglet for masonry conditions. All corner tabs shall extend to a minimum of 3-inches (3") past the plane of the corner.

Taper cut and remove portions of the counter flashing hem and corner tabs to allow the pieces to seat/nest tightly into the zee closure, and against the vertical facet. Provide 3 beads of butyl sealant between pieces. Overlap the counter flashing pieces 3-inches (3"). Crimp the counter flashing to the zee closure across the entire run length. Fasten counter flashings using screws with weathertight washers, as specified.

[Counterflashing shall be installed over all vertical base flashing elements that require a transitional flashing to overlap the base flashing and underlap the siding or trim elements.

Counterflashing shall extend to within 1-inch (1") of the plane of the finished roof, or the closure assembly flashing.

Counterflashing shall be broken with a longitudinal crease, to a degree adequate to provide a contact pressure (spring action) firmly against the base flashing.]

INSTALLATION OF RIDGE VENTILATION FLASHING

(Note to A/E: Where specified, and in conjunction with a fully vented soffit, the A/E shall calculate, verify, and specify, the appropriate balanced intake & exhaust ventilation adequate for the building. Additional detailing is required on the drawing set, if the area under roof panel system is vented.

Note: Typical steep slope commercial building roofs lack total ridge run lengths necessary to provide sufficient exhaust ventilation with an attic or an insulated deck assembly. A/E shall verify adequate ridge run lengths for specifying a ridge vent or specify an alternate exhaust ventilation.)

[Install rooftop attic ventilation per specifications listed herein, and in compliance with the manufacturer's additional detailed instructions, directly to the substrate as follows:

Prior to the installation of [Vented Ridge Cap] [Vented Zee Closure] the synthetic underlayment shall be cut back even with opening in ridge. Ridge vent opening shall not exceed 2.5-inches (2½") total width. Note: For openings over unheated / uninsulated cover / recover the opening with a 12-inch (12") wide strip of ice & water protection membrane sealed to the panel head lap.

[Installation of Vented Ridge Cap:

Note: Vented ridge cap shall be installed using the standard zee closure installation listed above.

Vented ridge cap shall be fabricated to have open hemmed edges that seat over the zee closure. Taper cut and remove portions of the hem to allow the cap pieces to seat/nest tightly. Provide 3 beads of butyl sealant between the top of zee closure and underside of the vented ridge cap. Position the vented ridge cap over the installed zee closure, and in contact with the vertical leg. Overlap the vented ridge cap pieces 3-inches (3"), with 3 beads of butyl sealant between pieces. Provide sealed metal end cap(s) at termination(s). Crimp the vented ridge cap to zee closure across entire run length. All interior lap joints, end laps, penetrations, and exposed fasteners shall be back caulked / caulked.]]

[Installation of Vented Zee Closure for Ridge Vent Openings:

Note: Vented zee closure shall be installed using the standard ridge cap installation listed above.

Install vented zee closures, set between panel legs, on both sides of the ridge. Notch the closures to fit tightly between the vertical legs, leaving no gaps for snow/water intrusion. Fasten 4-inches-on-center (4"o.c.). through double beaded butyl tape to metal panel only, do not fasten to substrate unless termination is a fixed point. All lap joints, end laps, penetrations, and exposed fasteners shall be back caulked / caulked.]

INSTALLATION OF MISCELLANEOUS ROOF FLASHING

Attach hood(s), covers, and miscellaneous flashing, to substrate and curb(s), with a minimum of two (2) screws with weathertight washers on each side. All miscellaneous conditions not listed herein shall be flashed using prefabricated units at all applicable locations. Note: All field fabricated miscellaneous flashings shall be reviewed, and approved, by the A/E prior to installation.

WORKMANSHIP

In part the following items may be cause for rejection or repair in whole or part of the roof system. Corrective action necessary will be determined by the SME, Division Representative and A/E.

- Blistering or cracking of any finish element of any kind.

- Denting or scratching of the metal panels, flashing, or assembly elements.

- Improper fastening / attachment of any component of the roofing system.

- Delamination or warping of the asphalt shingle roofing system from any surface.

- Disfigurement, delamination, warping, or damage to any of the flashing elements.

- Cuts, holes, tears, punctures, or damage to any of the roof system or flashing elements.

CLEANING

Inspect this and adjacent roof systems, gutters, downspouts, and the grounds below the work area and remove debris associated with this Project.

Repair or replace defaced shingle or disfigured finishes caused by Work in this Section. In areas where finished surfaces are soiled by any source caused by Work of this Section, consult with Manufacturer for cleaning advice, product recommendations, and conform to their instructions.

*** END OF SECTION ***